## standard_case
configuration
No of prosumers |  | 3
substations |  | hydraulic: | pipe + heat exchanger |  |  | thermal: | only heat exchanger
parametrization
fluid |  | rho=1000
(water) |  | cp=4200
mu=1.0016*(10**(-3))
valve |  | K_vs=2.5 |  |  |  | 0.3584
heat exchanger |  | dotV_nom=21.504 |  | Deltap_nom=155
|  | k_nom = 5270 |  | A = 1.13
pipe1 |  | L=15 | d_hy=0.022 | epsilon=0.011 | u_nom=0.4 | zeta_instal=10 | N_layers = 2 | d_layers = [0.022, 0.024, 0.062] | lambda_layers = [395, 0.04] | h_ir=3500 | h_or=float('inf')
pipe2 |  | L=5 | d_hy=0.022 | epsilon=0.011 | u_nom=0.4 | zeta_instal=3.5 | N_layers = 2 | d_layers = [0.022, 0.024, 0.062] | lambda_layers = [395, 0.04] | h_ir=3500 | h_or=float('inf')
Scenario
T_soil |  | 12 °C
df
participation prosumers |  | pi: 1
T_in_sec | for producers | 65 °C | [5 empty] | ss
T_in_sec | for consumers | 45 °C
dotV_sec | for producers | -10 l/min
dotV_sec | for consumers | 10 l/min

## variation possibilities
configuration
topology | radial
mesh
pump model | quadratic
linear
parametrization
pump dimensioning | pump1 | type: NMT PLUS ER 25/40-180 | n_nom: 4100 | dotV_max: 55.33 l/min | Deltap_max: 402.21 hPa
| pump2 | type: NMT PLUS ER 25/60-180 | n_nom: 4100 | dotV_max: 55.17 l/min | Deltap_max: 565.06 hPa
| pump3 | type: NMT PLUS ER 25/80-180 | n_nom: 4800 | dotV_max: 57.67 l/min | Deltap_max: 751.45 hPa
scenario
mu‘s for each prosumer (mode) | producer (1) or consumer (-1)
kappa for consumers | Kappa: 0.6
Kappa. 0.9
u for producers | U: 0.6
U: 0.9

## Cases overview
Base cases
For each base case (letters), scenarios (numbers) with different control inputs are calculated. All combinations of the options for kappa and u for all prosumers are calculated. Two options for kappa (0.6 and 0.9) and two options for u (0.6 and 0.9) lead for 3 prosumers to 8 scenarios for each base case (see table on the right). 2 additional scenarios result from using different volume flow and different inlet temperatures at the secondary side.
|  |  | X-1 | X-2 | X-3 | X-4 | X-5 | X-6 | X-7 | X-8 | X-9 | X-10
|  | prosumer1 | 0.9 | 0.6 | 0.9 | 0.6 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9
|  | prosumer2 | 0.9 | 0.6 | 0.6 | 0.9 | 0.6 | 0.9 | 0.6 | 0.9 | 0.9 | 0.9
|  | prosumer3 | 0.9 | 0.6 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.6 | 0.9 | 0.9
[11 empty] | T_sec_in | dotV_sec_in
For cases with equally dimensioned pumps, pump1 is used. For cases with differently dimensioned cases pump3 is used as big pump.
Base case A | radial, 2 consumers, 1 producer in center, pump (quadratic)
Base case B | radial, 2 producers, 1 consumer in center, equally dimensioned pumps (quadratic)
Base case C | radial, 2 consumers, 1 producer at edge, pump (quadratic)
Base case D | radial, 2 producers, 1 consumer at edge, equally dimensioned pumps (quadratic)
Base case E | meshed, 2 consumers, 1 producer, pump (quadratic)
Base case F | meshed, 2 producers, 1 consumer, equally dimensioned pumps (quadratic)
(Base case G) | radial, 2 producers, 1 consumer in center, differently dimensioned pumps (quadratic)
(Base case H) | radial, 2 producers, 1 consumer at edge, differently dimensioned pumps (quadratic)
(Base case I) | meshed, 2 producers, 1 consumer, differently dimensioned pumps (quadratic)
((Base case J)) | radial, 2 producers, 1 consumer in center, equally dimensioned pumps (linear)
((Base case K)) | radial, 2 producers, 1 consumer in center, differently dimensioned pumps (linear)
lin
lin
lin
lin

## Case_A
Case A |  | radial, 2 consumers, 1 producer in center, pump (quadratic)
pump1 | type: NMT PLUS ER 25/40-180 |  |  | n_nom: 4100 |  | dotV_max: 55.33 l/min |  | Deltap_max: 402.21 hPa
for A-9: |  | T_1_sec_c = 40 °C |  | T_3_sec_c = 50 °C
for A-10: |  | dotV_1_sec = 15 l/min |  | dotV_2_sec = -20 l/min
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim | dotV_1 | dotV_2 | dotV_3 | dotV_1h_2h | dotV_2h_3h | dotV_1h_1c | dotV_2h_2c | dotV_3h_3c | dotV_1c_2c | dotV_2c_3c | Deltap_1h_2h | Deltap_2h_3h | Deltap_1h_1c | Deltap_2h_2c | Deltap_3h_3c | Deltap_1c_2c | Deltap_2c_3c | T_1h_2h | T_1h_1c | T_2h_1h | T_2h_3h | T_2h_2c | T_3h_2h | T_3h_3c | T_1c_1h | T_1c_2c | T_2c_2h | T_2c_1c | T_2c_3c | T_3c_3h | T_3c_2c | T_PSM1h | T_PSM1c | T_PSM2h | T_PSM2c | T_PSM3h | T_PSM3c
A-01 | -6488.6248 | 13594.0204 | -6488.6248 | -616.7708 | 56.1106 | 45.5771 | 56.3956 | 45.3616 | 56.1106 | 45.5771 | 54.2695 | 45 | 65 | 45.58 | 54.2695 | 45 | 8.8 | -17.6001 | 8.8 | 10 | -10 | 10 | -90.2064 | -144.543 | -90.2064 | 10 | -10 | 10 | -8.8 | 8.8 | 8.8 | -17.6001 | 8.8 | 8.8 | -8.8 | 27.1683 | -27.1683 | -90.2064 | -144.543 | -90.2064 | -27.1683 | 27.1683 | 56.1106 | 56.1106 | 56.3956 | 56.3956 | 56.3956 | 56.1106 | 56.1106 | 45.5771 | 45.5771 | 45.3616 | 45.3616 | 45.3616 | 45.5771 | 45.5771 | 54.2695 | 45 | 65 | 45.58 | 54.2695 | 45
A-02 | -6208.8304 | 13074.2402 | -6208.8304 | -656.5794 | 61.6441 | 45.0045 | 62.1748 | 44.6554 | 61.6441 | 45.0045 | 53.8698 | 45 | 65 | 46.3225 | 53.8698 | 45 | 5.3305 | -10.661 | 5.3305 | 10 | -10 | 10 | -58.3556 | -78.2927 | -58.3556 | 10 | -10 | 10 | -5.3305 | 5.3305 | 5.3305 | -10.661 | 5.3305 | 5.3305 | -5.3305 | 9.9686 | -9.9686 | -58.3556 | -78.2927 | -58.3556 | -9.9686 | 9.9686 | 61.6441 | 61.6441 | 62.1748 | 62.1748 | 62.1748 | 61.6441 | 61.6441 | 45.0045 | 45.0045 | 44.6554 | 44.6554 | 44.6554 | 45.0045 | 45.0045 | 53.8698 | 45 | 65 | 46.3225 | 53.8698 | 45
A-03 | -6938.4866 | 13277.053 | -5686.5516 | -652.0147 | 61.1122 | 45.0311 | 61.5659 | 44.6866 | 61.0152 | 45.002 | 54.9121 | 45 | 65 | 46.0328 | 53.1236 | 45 | 6.1638 | -11.2369 | 5.0731 | 10 | -10 | 10 | -44.2558 | -70.9137 | -52.8556 | 10 | -10 | 10 | -6.1638 | 5.0731 | 6.1638 | -11.2369 | 5.0731 | 6.1638 | -5.0731 | 13.3289 | -9.029 | -44.2558 | -70.9137 | -52.8556 | -13.3289 | 9.029 | 61.1122 | 61.1122 | 61.5659 | 61.5659 | 61.5659 | 61.0152 | 61.0152 | 45.0311 | 45.0311 | 44.6866 | 44.7288 | 44.6354 | 45.002 | 45.002 | 54.9121 | 45 | 65 | 46.0328 | 53.1236 | 45
A-04 | -6550.2957 | 13722.5522 | -6550.2957 | -621.9609 | 57.0186 | 45.3155 | 57.3389 | 45.0801 | 57.0186 | 45.3155 | 54.3576 | 45 | 65 | 45.3964 | 54.3576 | 45 | 7.9958 | -15.9915 | 7.9958 | 10 | -10 | 10 | -131.3001 | -176.1586 | -131.3001 | 10 | -10 | 10 | -7.9958 | 7.9958 | 7.9958 | -15.9915 | 7.9958 | 7.9958 | -7.9958 | 22.4292 | -22.4292 | -131.3001 | -176.1586 | -131.3001 | -22.4292 | 22.4292 | 57.0186 | 57.0186 | 57.3389 | 57.3389 | 57.3389 | 57.0186 | 57.0186 | 45.3155 | 45.3155 | 45.0801 | 45.0801 | 45.0801 | 45.3155 | 45.3155 | 54.3576 | 45 | 65 | 45.3964 | 54.3576 | 45
A-05 | -5686.5516 | 13277.053 | -6938.4866 | -652.0147 | 61.0152 | 45.002 | 61.5659 | 44.6866 | 61.1122 | 45.0311 | 53.1236 | 45 | 65 | 46.0328 | 54.9121 | 45 | 5.0731 | -11.2369 | 6.1638 | 10 | -10 | 10 | -52.8556 | -70.9137 | -44.2558 | 10 | -10 | 10 | -5.0731 | 6.1638 | 5.0731 | -11.2369 | 6.1638 | 5.0731 | -6.1638 | 9.029 | -13.3289 | -52.8556 | -70.9137 | -44.2558 | -9.029 | 13.3289 | 61.0152 | 61.0152 | 61.5659 | 61.5659 | 61.5659 | 61.1122 | 61.1122 | 45.002 | 45.002 | 44.6866 | 44.6354 | 44.7288 | 45.0311 | 45.0311 | 53.1236 | 45 | 65 | 46.0328 | 54.9121 | 45
A-06 | -6022.5894 | 13603.334 | -6961.1374 | -619.6072 | 56.5069 | 45.2006 | 56.8396 | 45.3102 | 56.5656 | 45.8099 | 53.6037 | 45 | 65 | 45.5667 | 54.9445 | 45 | 7.6096 | -16.8554 | 9.2457 | 10 | -10 | 10 | -118.9252 | -159.5558 | -99.5756 | 10 | -10 | 10 | -7.6096 | 9.2457 | 7.6096 | -16.8554 | 9.2457 | 7.6096 | -9.2457 | 20.3153 | -29.9901 | -118.9252 | -159.5558 | -99.5756 | -20.3153 | 29.9901 | 56.5069 | 56.5069 | 56.8396 | 56.8396 | 56.8396 | 56.5656 | 56.5656 | 45.2006 | 45.2006 | 45.3102 | 44.9542 | 45.6032 | 45.8099 | 45.8099 | 53.6037 | 45 | 65 | 45.5667 | 54.9445 | 45
A-07 | -6387.1173 | 13422.2665 | -6387.1173 | -648.032 | 60.5691 | 45.0161 | 61.0406 | 44.6986 | 60.5691 | 45.0161 | 54.1245 | 45 | 65 | 45.8253 | 54.1245 | 45 | 5.8667 | -11.7334 | 5.8667 | 10 | -10 | 10 | -40.0917 | -64.2413 | -40.0917 | 10 | -10 | 10 | -5.8667 | 5.8667 | 5.8667 | -11.7334 | 5.8667 | 5.8667 | -5.8667 | 12.0748 | -12.0748 | -40.0917 | -64.2413 | -40.0917 | -12.0748 | 12.0748 | 60.5691 | 60.5691 | 61.0406 | 61.0406 | 61.0406 | 60.5691 | 60.5691 | 45.0161 | 45.0161 | 44.6986 | 44.6986 | 44.6986 | 45.0161 | 45.0161 | 54.1245 | 45 | 65 | 45.8253 | 54.1245 | 45
A-08 | -6961.1374 | 13603.334 | -6022.5894 | -619.6072 | 56.5656 | 45.8099 | 56.8396 | 45.3102 | 56.5069 | 45.2006 | 54.9445 | 45 | 65 | 45.5667 | 53.6037 | 45 | 9.2457 | -16.8554 | 7.6096 | 10 | -10 | 10 | -99.5756 | -159.5558 | -118.9252 | 10 | -10 | 10 | -9.2457 | 7.6096 | 9.2457 | -16.8554 | 7.6096 | 9.2457 | -7.6096 | 29.9901 | -20.3153 | -99.5756 | -159.5558 | -118.9252 | -29.9901 | 20.3153 | 56.5656 | 56.5656 | 56.8396 | 56.8396 | 56.8396 | 56.5069 | 56.5069 | 45.8099 | 45.8099 | 45.3102 | 45.6032 | 44.9542 | 45.2006 | 45.2006 | 54.9445 | 45 | 65 | 45.5667 | 53.6037 | 45
A-09 | -9408.6454 | 13594.0204 | -3568.6042 | -616.7708 | 56.1106 | 40.8369 | 56.3956 | 45.3616 | 56.1106 | 50.3174 | 53.4409 | 40 | 65 | 45.58 | 55.098 | 50 | 8.8 | -17.6001 | 8.8 | 10 | -10 | 10 | -90.2064 | -144.543 | -90.2064 | 10 | -10 | 10 | -8.8 | 8.8 | 8.8 | -17.6001 | 8.8 | 8.8 | -8.8 | 27.1683 | -27.1683 | -90.2064 | -144.543 | -90.2064 | -27.1683 | 27.1683 | 56.1106 | 56.1106 | 56.3956 | 56.3956 | 56.3956 | 56.1106 | 56.1106 | 40.8369 | 40.8369 | 45.3616 | 40.6517 | 50.0714 | 50.3174 | 50.3174 | 53.4409 | 40 | 65 | 45.58 | 55.098 | 50
A-10 | -10432.3062 | 21062.9557 | -9967.0014 | -663.6481 | 62.0667 | 45.1312 | 62.3902 | 45.2937 | 62.0667 | 45.8865 | 54.9355 | 45 | 65 | 49.955 | 59.2386 | 45 | 8.8 | -17.6001 | 8.8 | 15 | -20 | 10 | -90.2064 | -144.543 | -90.2064 | 15 | -20 | 10 | -8.8 | 8.8 | 8.8 | -17.6001 | 8.8 | 8.8 | -8.8 | 27.1683 | -27.1683 | -90.2064 | -144.543 | -90.2064 | -27.1683 | 27.1683 | 62.0667 | 62.0667 | 62.3902 | 62.3902 | 62.3902 | 62.0667 | 62.0667 | 45.1312 | 45.1312 | 45.2937 | 44.9184 | 45.669 | 45.8865 | 45.8865 | 54.9355 | 45 | 65 | 49.955 | 59.2386 | 45
ProsNet results:
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim
A-1 | -6097.56 | 12814.88 | -6097.56 | -619.76 | 56.05 | 46.26 | 56.33 | 46.04 | 56.05 | 46.26 | 53.74 | 45 | 65 | 46.62 | 53.74 | 45 | 8.93 | -17.86 | 8.93 | 10 | -10 | 10 | -91.57 | -141.44 | -91.57
A-2 | -5752.83 | 12152.18 | -5752.83 | -646.52 | 60.63 | 45.18 | 61.15 | 44.83 | 60.63 | 45.18 | 53.25 | 45 | 65 | 47.57 | 53.25 | 45 | 5.34 | -10.68 | 5.34 | 10 | -10 | 10 | -58.49 | -78.11 | -58.49
A-3 | -6414.41 | 12340.68 | -5282.9 | -643.38 | 60.19 | 45.39 | 60.63 | 44.94 | 60.09 | 45.13 | 54.2 | 45 | 65 | 47.3 | 52.58 | 45 | 6.21 | -11.27 | 5.06 | 10 | -10 | 10 | -44.67 | -70.48 | -52.65
A-4 | -6134 | 12891.37 | -6134 | -623.38 | 56.83 | 45.95 | 57.15 | 45.71 | 56.83 | 45.95 | 53.8 | 45 | 65 | 46.51 | 53.8 | 45 | 8.08 | -16.16 | 8.08 | 10 | -10 | 10 | -133.02 | -174.6 | -133.02
A-5 | -5282.9 | 12340.68 | -6414.41 | -643.38 | 60.09 | 45.13 | 60.63 | 44.94 | 60.19 | 45.39 | 52.58 | 45 | 65 | 47.3 | 54.2 | 45 | 5.06 | -11.27 | 6.21 | 10 | -10 | 10 | -52.65 | -70.48 | -44.67
A-6 | -5680.87 | 12811.03 | -6508.49 | -621.68 | 56.38 | 45.74 | 56.71 | 45.96 | 56.45 | 46.55 | 53.15 | 45 | 65 | 46.63 | 54.33 | 45 | 7.65 | -17.08 | 9.43 | 10 | -10 | 10 | -119.4 | -157.06 | -101.98
A-7 | -5933.79 | 12508.05 | -5933.79 | -640.46 | 59.73 | 45.29 | 60.19 | 44.97 | 59.73 | 45.29 | 53.51 | 45 | 65 | 47.06 | 53.51 | 45 | 5.89 | -11.78 | 5.89 | 10 | -10 | 10 | -40.22 | -63.67 | -40.22
A-8 | -6508.49 | 12811.03 | -5680.87 | -621.68 | 56.45 | 46.55 | 56.71 | 45.96 | 56.38 | 45.74 | 54.33 | 45 | 65 | 46.63 | 53.15 | 45 | 9.43 | -17.08 | 7.65 | 10 | -10 | 10 | -101.98 | -157.06 | -119.4
A-9 | -8856.46 | 12814.88 | -3338.65 | -619.76 | 56.05 | 41.83 | 56.33 | 46.04 | 56.05 | 50.69 | 52.7 | 40 | 65 | 46.62 | 54.79 | 50 | 8.93 | -17.86 | 8.93 | 10 | -10 | 10 | -91.57 | -141.44 | -91.57
A-10 | -10079.7 | 19980.39 | -9236.02 | -664.68 | 61.74 | 45.55 | 62.06 | 46.01 | 61.74 | 46.9 | 54.64 | 45 | 65 | 50.67 | 58.24 | 45 | 8.93 | -17.86 | 8.93 | 15 | -20 | 10 | -91.57 | -141.44 | -91.57

## Case_B
Case B |  | radial, 2 producers, 1 consumer in center, equally dimensioned pumps (quadratic)
pump1 | type: NMT PLUS ER 25/40-180 |  |  | n_nom: 4100 |  | dotV_max: 55.33 l/min |  | Deltap_max: 402.21 hPa
for B-9: |  | T_1_sec_h = 50 °C |  | T_2_sec_c = 40 °C
for B-10: |  | dotV_1_sec = -20 l/min |  | dotV_2_sec = 15 l/min
ProsNet results:
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim
B-1 | 6577.35 | -12429.32 | 6577.35 | -725.38 | 64.21 | 51.58 | 63.82 | 51.88 | 64.21 | 51.58 | 65 | 55.57 | 62.82 | 45 | 65 | 55.57 | -7.47 | 14.94 | -7.47 | -10 | 10 | -10 | -289.77 | -253.75 | -289.77
B-2 | 5184.07 | -9685.34 | 5184.07 | -682.78 | 64.97 | 45.83 | 64.2 | 46.32 | 64.97 | 45.83 | 65 | 57.57 | 58.89 | 45 | 65 | 57.57 | -3.88 | 7.77 | -3.88 | -10 | 10 | -10 | -133.95 | -122.96 | -133.95
B-3 | 10420.53 | -10001.66 | 93.96 | -509.79 | 62.22 | 47.35 | 61.94 | 47.61 | 31.82 | 64.98 | 65 | 50.06 | 59.34 | 45 | 65 | 64.87 | -10.05 | 10.01 | 0.04 | -10 | 10 | -10 | -265.01 | -203.13 | -203.09
B-4 | 5971.21 | -11245.63 | 5971.21 | -696.78 | 64.87 | 47.53 | 64.27 | 47.94 | 64.87 | 47.53 | 65 | 56.44 | 61.13 | 45 | 65 | 56.44 | -4.94 | 9.87 | -4.94 | -10 | 10 | -10 | -128.77 | -111.73 | -128.77
B-5 | 93.57 | -10001.64 | 10420.68 | -509.74 | 32.12 | 64.98 | 61.94 | 47.61 | 62.22 | 47.35 | 65 | 64.87 | 59.34 | 45 | 65 | 50.06 | 0.04 | 10.01 | -10.05 | -10 | 10 | -10 | -203.09 | -203.13 | -265.01
B-6 | 3.33 | -9868.75 | 10257.12 | -389.04 | 20.75 | 23.73 | 60.79 | 48.82 | 61.02 | 48.6 | 65 | 65 | 59.15 | 45 | 65 | 50.29 | 0.02 | 11.83 | -11.84 | -10 | 10 | -10 | -159.73 | -159.74 | -243.36
B-7 | 6338.41 | -11967.32 | 6338.41 | -709.48 | 64.7 | 49.2 | 64.19 | 49.56 | 64.7 | 49.2 | 65 | 55.91 | 62.16 | 45 | 65 | 55.91 | -5.87 | 11.73 | -5.87 | -10 | 10 | -10 | -301.66 | -278.4 | -301.66
B-8 | 10256.29 | -9868.95 | 3.52 | -380.86 | 61.02 | 48.6 | 60.79 | 48.82 | 18.4 | 21.55 | 65 | 50.29 | 59.15 | 45 | 65 | 64.99 | -11.84 | 11.83 | 0.02 | -10 | 10 | -10 | -243.36 | -159.74 | -159.73
B-9 | 2074.41 | -10880.38 | 9426.91 | -620.94 | 49.75 | 45.77 | 56.47 | 46.03 | 63.87 | 45.77 | 50 | 47.03 | 55.6 | 40 | 65 | 51.48 | -7.47 | 14.94 | -7.47 | -10 | 10 | -10 | -289.77 | -253.75 | -289.77
B-10 | 8760.31 | -16350.95 | 8290.22 | -699.57 | 64.91 | 48.09 | 64.06 | 48.36 | 64 | 48.09 | 65 | 58.72 | 60.63 | 45 | 65 | 53.11 | -7.47 | 14.94 | -7.47 | -20 | 15 | -10 | -289.77 | -253.75 | -289.77

## Case_C
Case C |  | radial, 2 consumers, 1 producer at edge, pump (quadratic)
pump1 | type: NMT PLUS ER 25/40-180 |  |  | n_nom: 4100 |  | dotV_max: 55.33 l/min |  | Deltap_max: 402.21 hPa
for C-9: |  | T_1_sec_c = 50 °C |  | T_2_sec_c = 40 °C
for C-10: |  | dotV_1_sec = -20 l/min |  | dotV_2_sec = 15 l/min
ProsNet results:
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim
C-1 | 12830.88 | -6726.35 | -5477.61 | -626.92 | 58.06 | 45.52 | 57.88 | 46.08 | 57.48 | 45.4 | 65 | 46.6 | 54.65 | 45 | 52.86 | 45 | -14.67 | 8.17 | 6.5 | -10 | 10 | 10 | -200.96 | -76.86 | -48.85
C-2 | 11234.99 | -5786.38 | -4792.78 | -655.83 | 62.67 | 44.66 | 62.35 | 45.11 | 61.67 | 45.04 | 65 | 48.89 | 53.3 | 45 | 51.87 | 45 | -8.95 | 4.81 | 4.13 | -10 | 10 | 10 | -97.68 | -47.63 | -35.24
C-3 | 12801.22 | -6530.41 | -5639.74 | -631.06 | 58.74 | 45.28 | 58.54 | 45.73 | 58.13 | 45.37 | 65 | 46.64 | 54.36 | 45 | 53.09 | 45 | -13.65 | 7.31 | 6.34 | -10 | 10 | 10 | -217.52 | -108.97 | -82.21
C-4 | 11482.67 | -6660.93 | -4168.93 | -652.8 | 62.29 | 44.78 | 61.98 | 45.28 | 61.22 | 45.02 | 65 | 48.53 | 54.55 | 45 | 50.98 | 45 | -9.41 | 5.72 | 3.69 | -10 | 10 | 10 | -92.81 | -37.93 | -28.08
C-5 | 11423.48 | -5354.06 | -5414.57 | -654.85 | 62.43 | 44.68 | 62.12 | 45.07 | 61.52 | 45.09 | 65 | 48.62 | 52.68 | 45 | 52.76 | 45 | -9.23 | 4.5 | 4.73 | -10 | 10 | 10 | -94.74 | -41.76 | -26
C-6 | 11628.5 | -6236.82 | -4739.66 | -652.01 | 62.11 | 44.75 | 61.81 | 45.2 | 61.15 | 45.04 | 65 | 48.32 | 53.94 | 45 | 51.8 | 45 | -9.61 | 5.39 | 4.22 | -10 | 10 | 10 | -90.66 | -33.67 | -20.8
C-7 | 12854.49 | -6045.14 | -6179.02 | -630.33 | 58.41 | 45.33 | 58.23 | 45.53 | 57.87 | 45.68 | 65 | 46.57 | 53.67 | 45 | 53.86 | 45 | -14.09 | 6.83 | 7.27 | -10 | 10 | 10 | -210.45 | -95.22 | -60.93
C-8 | 12693.8 | -7147.21 | -4918.21 | -628.37 | 58.33 | 45.65 | 58.15 | 46.38 | 57.69 | 45.2 | 65 | 46.8 | 55.25 | 45 | 52.05 | 45 | -14.35 | 8.71 | 5.65 | -10 | 10 | 10 | -206.26 | -87.11 | -65.39
C-9 | 5052.54 | -3723.64 | -800.91 | -527.98 | 47.27 | 42.33 | 47.13 | 40.6 | 46.82 | 45.06 | 50 | 42.75 | 45.34 | 40 | 46.15 | 45 | -14.67 | 8.17 | 6.5 | -10 | 10 | 10 | -200.96 | -76.86 | -48.85
C-10 | 18425.31 | -10043.24 | -7715.08 | -666.98 | 63.22 | 45.21 | 63.02 | 45.4 | 62.58 | 45.56 | 65 | 51.79 | 54.6 | 45 | 56.06 | 45 | -14.67 | 8.17 | 6.5 | -20 | 15 | 10 | -200.96 | -76.86 | -48.85

## Case_D
Case D |  | radial, 2 producers, 1 consumer at edge, equally dimensioned pumps (quadratic)
pump1 | type: NMT PLUS ER 25/40-180 |  |  | n_nom: 4100 |  | dotV_max: 55.33 l/min |  | Deltap_max: 402.21 hPa
for D-9: |  | T_1_sec_c = 40 °C |  | T_2_sec_c = 50 °C
for D-10: |  | dotV_1_sec = 15 l/min |  | dotV_2_sec = -20 l/min
ProsNet results:
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim
D-1 | -12101.09 | 7409.14 | 5407.31 | -715.36 | 63.88 | 50.43 | 64 | 50.26 | 64.86 | 49.85 | 62.35 | 45 | 65 | 54.38 | 65 | 57.25 | 12.9 | -7.73 | -5.17 | 10 | -10 | -10 | -189.72 | -287.57 | -306.06
D-2 | -8940.25 | 5572.19 | 4045.2 | -677.14 | 64.13 | 45.86 | 64.95 | 45.59 | 65 | 44.94 | 57.82 | 45 | 65 | 57.01 | 65 | 59.2 | 7.02 | -4.13 | -2.89 | 10 | -10 | -10 | -100.64 | -132.84 | -138.06
D-3 | -10267.22 | 6460.72 | 4492.78 | -686.29 | 64.2 | 46.83 | 64.84 | 46.6 | 64.99 | 46.03 | 59.72 | 45 | 65 | 55.74 | 65 | 58.56 | 8.48 | -5.08 | -3.4 | 10 | -10 | -10 | -82.63 | -127.99 | -136.07
D-4 | -9971.86 | 10416.09 | 129.69 | -573.77 | 61.89 | 47.6 | 62.17 | 47.36 | 40.8 | 65 | 59.3 | 45 | 65 | 50.06 | 65 | 64.81 | 10.01 | -10.09 | 0.08 | 10 | -10 | -10 | -203.18 | -264.61 | -264.54
D-5 | -9559.3 | 9.46 | 10225.07 | -675.22 | 62.1 | 47.09 | 62.4 | 65 | 62.73 | 46.77 | 58.71 | 45 | 65 | 64.99 | 65 | 50.34 | 9.13 | 0.05 | -9.19 | 10 | -10 | -10 | -169.56 | -221.55 | -274.09
D-6 | -11509.41 | 7169.04 | 5041.75 | -701.39 | 64.13 | 48.62 | 64.52 | 48.42 | 64.95 | 47.94 | 61.5 | 45 | 65 | 54.72 | 65 | 57.77 | 10.64 | -6.39 | -4.25 | 10 | -10 | -10 | -229.35 | -298.06 | -311.1
D-7 | -9730.99 | 8.48 | 10398 | -675.48 | 61.28 | 47.96 | 61.28 | 64.94 | 61.81 | 47.63 | 58.95 | 45 | 65 | 64.99 | 65 | 50.09 | 10.48 | 0.04 | -10.51 | 10 | -10 | -10 | -125.72 | -192.53 | -259.76
D-8 | -9845.56 | 10278.27 | 121.76 | -554.04 | 60.75 | 48.81 | 60.99 | 48.58 | 37.92 | 65 | 59.12 | 45 | 65 | 50.26 | 65 | 64.83 | 11.82 | -11.88 | 0.06 | 10 | -10 | -10 | -159.51 | -242.82 | -242.76
D-9 | -9786.42 | 2890.82 | 7529.11 | -633.51 | 55.27 | 44.39 | 49.61 | 44.25 | 64.8 | 43.9 | 54.03 | 40 | 50 | 45.85 | 65 | 54.2 | 12.9 | -7.73 | -5.17 | 10 | -10 | -10 | -189.72 | -287.57 | -306.06
D-10 | -12197.08 | 4407.97 | 8403.73 | -614.61 | 55.46 | 41.9 | 49.95 | 41.77 | 64.78 | 41.45 | 51.66 | 40 | 50 | 46.84 | 65 | 52.95 | 12.9 | -7.73 | -5.17 | 15 | -20 | -10 | -189.72 | -287.57 | -306.06

## Case_E
Case E |  | meshed, 2 consumers, 1 producer, pump (quadratic)
pump1 | type: NMT PLUS ER 25/40-180 |  |  | n_nom: 4100 |  | dotV_max: 55.33 l/min |  | Deltap_max: 402.21 hPa
for E-9: |  | T_1_sec_c = 40 °C |  | T_3_sec_c = 50 °C
for E-10: |  | dotV_1_sec = 15 l/min |  | dotV_2_sec = -20 l/min
ProsNet results:
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim | dotV_bypass_h
E-1 | -6097.56 | 12814.88 | -6097.56 | -619.84 | 56.05 | 46.26 | 56.33 | 46.04 | 56.05 | 46.26 | 53.74 | 45 | 65 | 46.62 | 53.74 | 45 | 8.93 | -17.86 | 8.93 | 10 | -10 | 10 | -91.57 | -141.44 | -91.57 | 0
E-2 | -5752.83 | 12152.18 | -5752.83 | -646.6 | 60.63 | 45.18 | 61.15 | 44.83 | 60.63 | 45.18 | 53.25 | 45 | 65 | 47.57 | 53.25 | 45 | 5.34 | -10.68 | 5.34 | 10 | -10 | 10 | -58.49 | -78.11 | -58.49 | 0
E-3 | -6403.28 | 12430.85 | -5085.04 | -942.53 | 59.7 | 45.45 | 60.58 | 44.81 | 60.09 | 45.1 | 54.18 | 45 | 65 | 47.17 | 52.29 | 45 | 6.44 | -11.31 | 4.86 | 10 | -10 | 10 | -47.98 | -70.08 | -48.66 | 0.74
E-4 | -6134 | 12891.37 | -6134 | -623.46 | 56.83 | 45.95 | 57.15 | 45.71 | 56.83 | 45.95 | 53.8 | 45 | 65 | 46.51 | 53.8 | 45 | 8.08 | -16.16 | 8.08 | 10 | -10 | 10 | -133.02 | -174.6 | -133.02 | 0
E-5 | -5085.04 | 12430.85 | -6403.28 | -942.53 | 60.09 | 45.1 | 60.58 | 44.81 | 59.7 | 45.45 | 52.29 | 45 | 65 | 47.17 | 54.18 | 45 | 4.86 | -11.31 | 6.44 | 10 | -10 | 10 | -48.66 | -70.08 | -47.98 | -0.74
E-6 | -5507.59 | 12862.11 | -6434.68 | -919.83 | 56.36 | 45.63 | 56.66 | 45.89 | 56.12 | 46.67 | 52.9 | 45 | 65 | 46.56 | 54.23 | 45 | 7.36 | -17.13 | 9.77 | 10 | -10 | 10 | -110.49 | -156.15 | -109.39 | -1.15
E-7 | -5933.79 | 12508.05 | -5933.79 | -640.54 | 59.73 | 45.29 | 60.19 | 44.97 | 59.73 | 45.29 | 53.51 | 45 | 65 | 47.06 | 53.51 | 45 | 5.89 | -11.78 | 5.89 | 10 | -10 | 10 | -40.22 | -63.67 | -40.22 | 0
E-8 | -6434.68 | 12862.11 | -5507.59 | -919.83 | 56.12 | 46.67 | 56.66 | 45.89 | 56.36 | 45.63 | 54.23 | 45 | 65 | 46.56 | 52.9 | 45 | 9.77 | -17.13 | 7.36 | 10 | -10 | 10 | -109.39 | -156.15 | -110.49 | 1.15
E-9 | -8856.46 | 12814.88 | -3338.65 | -619.84 | 56.05 | 41.83 | 56.33 | 46.04 | 56.05 | 50.69 | 52.7 | 40 | 65 | 46.62 | 54.79 | 50 | 8.93 | -17.86 | 8.93 | 10 | -10 | 10 | -91.57 | -141.44 | -91.57 | 0
E-10 | -10079.7 | 19980.39 | -9236.02 | -664.76 | 61.74 | 45.55 | 62.06 | 46.01 | 61.74 | 46.9 | 54.64 | 45 | 65 | 50.67 | 58.24 | 45 | 8.93 | -17.86 | 8.93 | 15 | -20 | 10 | -91.57 | -141.44 | -91.57 | 0

## Case_F
Case F |  | meshed, 2 producers, 1 consumer, equally dimensioned pumps (quadratic)
pump1 | type: NMT PLUS ER 25/40-180 |  |  | n_nom: 4100 |  | dotV_max: 55.33 l/min |  | Deltap_max: 402.21 hPa
for F-9: |  | T_1_sec_c = 50 °C |  | T_2_sec_c = 40 °C
for F-10: |  | dotV_1_sec = -20 l/min |  | dotV_3_sec = 15 l/min
ProsNet results:
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim | dotV_bypass_h
F-1 | 5415.82 | -10145.17 | 5415.7 | -686.47 | 64.95 | 46.23 | 64.24 | 46.7 | 64.95 | 46.23 | 65 | 57.23 | 59.55 | 45 | 65 | 57.23 | -4.15 | 8.29 | -4.15 | -10 | 10 | -10 | -93.5 | -79.15 | -91.62 | 0
F-2 | 5184.07 | -9685.34 | 5184.07 | -682.86 | 64.97 | 45.83 | 64.2 | 46.32 | 64.97 | 45.83 | 65 | 57.57 | 58.89 | 45 | 65 | 57.57 | -3.88 | 7.77 | -3.88 | -10 | 10 | -10 | -133.95 | -122.96 | -133.95 | 0
F-3 | 10531.91 | -9545.58 | 18.42 | -1004.74 | 61.62 | 47.56 | 60.84 | 48.02 | 61 | 65 | 65 | 49.9 | 58.69 | 45 | 65 | 64.97 | -10.74 | 10.68 | 0.07 | -10 | 10 | -10 | -257.05 | -231.05 | -245.13 | -4.51
F-4 | 5415.75 | -10145.26 | 5415.75 | -686.33 | 64.95 | 46.23 | 64.24 | 46.7 | 64.95 | 46.23 | 65 | 57.23 | 59.55 | 45 | 65 | 57.23 | -4.15 | 8.29 | -4.15 | -10 | 10 | -10 | -91.8 | -79.15 | -91.62 | 0
F-5 | 18.42 | -9545.58 | 10531.91 | -1004.74 | 61 | 65 | 60.84 | 48.02 | 61.62 | 47.56 | 65 | 64.97 | 58.69 | 45 | 65 | 49.9 | 0.07 | 10.68 | -10.74 | -10 | 10 | -10 | -245.13 | -231.05 | -257.05 | 4.51
F-6 | 16.76 | -9401.49 | 10390.37 | -1005.64 | 59.75 | 64.99 | 59.66 | 49.24 | 60.29 | 48.81 | 65 | 64.98 | 58.48 | 45 | 65 | 50.1 | 0.05 | 12.94 | -12.98 | -10 | 10 | -10 | -210.88 | -190.85 | -227.5 | 5.44
F-7 | 5415.75 | -10145.24 | 5415.76 | -686.32 | 64.95 | 46.23 | 64.24 | 46.7 | 64.95 | 46.23 | 65 | 57.23 | 59.55 | 45 | 65 | 57.23 | -4.15 | 8.29 | -4.15 | -10 | 10 | -10 | -154.73 | -140.06 | -152.53 | 0
F-8 | 10390.37 | -9401.49 | 16.76 | -1005.64 | 60.29 | 48.81 | 59.66 | 49.24 | 59.75 | 64.99 | 65 | 50.1 | 58.48 | 45 | 65 | 64.98 | -12.98 | 12.94 | 0.05 | -10 | 10 | -10 | -227.5 | -190.85 | -210.88 | -5.44
F-9 | 2074.41 | -10880.38 | 9426.91 | -621.02 | 49.75 | 45.77 | 56.47 | 46.03 | 63.87 | 45.77 | 50 | 47.03 | 55.6 | 40 | 65 | 51.48 | -7.47 | 14.94 | -7.47 | -10 | 10 | -10 | -289.77 | -253.75 | -289.77 | 0
F-10 | 5427.3 | -10165.93 | 5425.46 | -686.97 | 65 | 46.23 | 64.28 | 46.7 | 64.99 | 46.23 | 65 | 61.11 | 59.58 | 45 | 65 | 59.81 | -4.15 | 8.29 | -4.15 | -20 | 10 | -15 | -91.95 | -79.15 | -91.62 | 0