## standard_case
configuration
No of prosumers |  | 3
substations |  | hydraulic: | pipe + heat exchanger |  |  | thermal: | only heat exchanger
parametrization
fluid |  | rho=1000
(water) |  | cp=4200
mu=1.0016*(10**(-3))
valve |  | K_vs=2.5 |  |  |  | 0.3584
heat exchanger |  | dotV_nom=21.504 |  | Deltap_nom=155
|  | k_nom = 5270 |  | A = 1.13
pipe1 |  | L=15 | d_hy=0.022 | epsilon=0.011 | u_nom=0.4 | zeta_instal=10 | N_layers = 2 | d_layers = [0.022, 0.024, 0.062] | lambda_layers = [395, 0.04] | h_ir=3500 | h_or=float('inf')
pipe2 |  | L=5 | d_hy=0.022 | epsilon=0.011 | u_nom=0.4 | zeta_instal=3.5 | N_layers = 2 | d_layers = [0.022, 0.024, 0.062] | lambda_layers = [395, 0.04] | h_ir=3500 | h_or=float('inf')
Scenario
T_soil |  | 12 °C
df
participation prosumers |  | pi: 1
T_in_sec | for producers | 65 °C | [5 empty] | ss
T_in_sec | for consumers | 45 °C
dotV_sec | for producers | -10 l/min
dotV_sec | for consumers | 10 l/min

## variation possibilities
configuration
topology | radial
mesh
pump model | quadratic
linear
parametrization
pump dimensioning | pump1 | type: NMT PLUS ER 25/40-180 | n_nom: 4100 | dotV_max: 55.33 l/min | Deltap_max: 402.21 hPa
| pump2 | type: NMT PLUS ER 25/60-180 | n_nom: 4100 | dotV_max: 55.17 l/min | Deltap_max: 565.06 hPa
| pump3 | type: NMT PLUS ER 25/80-180 | n_nom: 4800 | dotV_max: 57.67 l/min | Deltap_max: 751.45 hPa
scenario
mu‘s for each prosumer (mode) | producer (1) or consumer (-1)
kappa for consumers | Kappa: 0.6
Kappa. 0.9
u for producers | U: 0.6
U: 0.9

## Cases overview
Base cases
For each base case (letters), scenarios (numbers) with different control inputs are calculated. All combinations of the options for kappa and u for all prosumers are calculated. Two options for kappa (0.6 and 0.9) and two options for u (0.6 and 0.9) lead for 3 prosumers to 8 scenarios for each base case (see table on the right). 2 additional scenarios result from using different volume flow and different inlet temperatures at the secondary side.
|  |  | X-1 | X-2 | X-3 | X-4 | X-5 | X-6 | X-7 | X-8 | X-9 | X-10
|  | prosumer1 | 0.9 | 0.6 | 0.9 | 0.6 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9
|  | prosumer2 | 0.9 | 0.6 | 0.6 | 0.9 | 0.6 | 0.9 | 0.6 | 0.9 | 0.9 | 0.9
|  | prosumer3 | 0.9 | 0.6 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.6 | 0.9 | 0.9
[11 empty] | T_sec_in | dotV_sec_in
For cases with equally dimensioned pumps, pump1 is used. For cases with differently dimensioned cases pump3 is used as big pump. |  | Variations in different lengths of the pipes between two prosumers equal to a more closed valve in one prosumer. Differently dimensioned pumps are covered by the cases where pumps run on different speeds. 3 prosumers is the optimal constellation to investigate, as networks with higher amount of prosumers can be subsumed to the 3-prosumer case by grouping some prosumers.
Base case A | radial, 2 consumers, 1 producer in center, pump (quadratic)
Base case B | radial, 2 producers, 1 consumer in center, equally dimensioned pumps (quadratic)
Base case C | radial, 2 consumers, 1 producer at edge, pump (quadratic)
Base case D | radial, 2 producers, 1 consumer at edge, equally dimensioned pumps (quadratic)
Base case E | meshed, 2 consumers, 1 producer, pump (quadratic)
Base case F | meshed, 2 producers, 1 consumer, equally dimensioned pumps (quadratic)
(Base case G) | radial, 2 producers, 1 consumer in center, differently dimensioned pumps (quadratic)
(Base case H) | radial, 2 producers, 1 consumer at edge, differently dimensioned pumps (quadratic)
(Base case I) | meshed, 2 producers, 1 consumer, differently dimensioned pumps (quadratic)
((Base case J)) | radial, 2 producers, 1 consumer in center, equally dimensioned pumps (linear)
((Base case K)) | radial, 2 producers, 1 consumer in center, differently dimensioned pumps (linear)
lin
lin
lin
lin

## Case_A
Case A |  | radial, 2 consumers, 1 producer in center, pump (quadratic)
pump1 | type: NMT PLUS ER 25/40-180 |  |  | n_nom: 4100 |  | dotV_max: 55.33 l/min |  | Deltap_max: 402.21 hPa
for A-9: |  | T_1_sec_c = 40 °C |  | T_3_sec_c = 50 °C
for A-10: |  | dotV_1_sec = 15 l/min |  | dotV_2_sec = -20 l/min
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim | dotV_1 | dotV_2 | dotV_3 | dotV_1h_2h | dotV_2h_3h | dotV_1h_1c | dotV_2h_2c | dotV_3h_3c | dotV_1c_2c | dotV_2c_3c | Deltap_1h_2h | Deltap_2h_3h | Deltap_1h_1c | Deltap_2h_2c | Deltap_3h_3c | Deltap_1c_2c | Deltap_2c_3c | T_1h_2h | T_1h_1c | T_2h_1h | T_2h_3h | T_2h_2c | T_3h_2h | T_3h_3c | T_1c_1h | T_1c_2c | T_2c_2h | T_2c_1c | T_2c_3c | T_3c_3h | T_3c_2c | T_PSM1h | T_PSM1c | T_PSM2h | T_PSM2c | T_PSM3h | T_PSM3c
A-01 | -6472.5848 | 13561.2089 | -6472.5848 | -616.0392 | 55.9624 | 45.6344 | 56.2416 | 45.4221 | 55.9624 | 45.6344 | 54.2465 | 45 | 65 | 45.6268 | 54.2465 | 45 | 8.9529 | -17.9059 | 8.9529 | 10 | -10 | 10 | -92.3274 | -142.322 | -92.3274 | 10 | -10 | 10 | -8.9529 | 8.9529 | 8.9529 | -17.9059 | 8.9529 | 8.9529 | -8.9529 | 24.9973 | -24.9973 | -92.3274 | -142.322 | -92.3274 | -24.9973 | 24.9973 | 55.9624 | 55.9624 | 56.2416 | 56.2416 | 56.2416 | 55.9624 | 55.9624 | 45.6344 | 45.6344 | 45.4221 | 45.4221 | 45.4221 | 45.6344 | 45.6344 | 54.2465 | 45 | 65 | 45.6268 | 54.2465 | 45
A-02 | -6239.7026 | 13134.772 | -6239.7026 | -655.3669 | 61.4924 | 45.0055 | 62.014 | 44.6613 | 61.4924 | 45.0055 | 53.9139 | 45 | 65 | 46.236 | 53.9139 | 45 | 5.4066 | -10.8133 | 5.4066 | 10 | -10 | 10 | -59.6544 | -77.8869 | -59.6544 | 10 | -10 | 10 | -5.4066 | 5.4066 | 5.4066 | -10.8133 | 5.4066 | 5.4066 | -5.4066 | 9.1162 | -9.1162 | -59.6544 | -77.8869 | -59.6544 | -9.1162 | 9.1162 | 61.4924 | 61.4924 | 62.014 | 62.014 | 62.014 | 61.4924 | 61.4924 | 45.0055 | 45.0055 | 44.6613 | 44.6613 | 44.6613 | 45.0055 | 45.0055 | 53.9139 | 45 | 65 | 46.236 | 53.9139 | 45
A-03 | -6993.474 | 13330.563 | -5686.5109 | -650.5781 | 60.9303 | 45.0391 | 61.3735 | 44.6964 | 60.8312 | 45.0024 | 54.9907 | 45 | 65 | 45.9563 | 53.1236 | 45 | 6.2869 | -11.4191 | 5.1322 | 10 | -10 | 10 | -45.5272 | -70.1799 | -53.7516 | 10 | -10 | 10 | -6.2869 | 5.1322 | 6.2869 | -11.4191 | 5.1322 | 6.2869 | -5.1322 | 12.3263 | -8.2142 | -45.5272 | -70.1799 | -53.7516 | -12.3263 | 8.2142 | 60.9303 | 60.9303 | 61.3735 | 61.3735 | 61.3735 | 60.8312 | 60.8312 | 45.0391 | 45.0391 | 44.6964 | 44.7425 | 44.6399 | 45.0024 | 45.0024 | 54.9907 | 45 | 65 | 45.9563 | 53.1236 | 45
A-04 | -6544.29 | 13709.6553 | -6544.29 | -621.0753 | 56.8757 | 45.3479 | 57.1905 | 45.1157 | 56.8757 | 45.3479 | 54.349 | 45 | 65 | 45.4148 | 54.349 | 45 | 8.1099 | -16.2199 | 8.1099 | 10 | -10 | 10 | -134.2225 | -175.2455 | -134.2225 | 10 | -10 | 10 | -8.1099 | 8.1099 | 8.1099 | -16.2199 | 8.1099 | 8.1099 | -8.1099 | 20.5115 | -20.5115 | -134.2225 | -175.2455 | -134.2225 | -20.5115 | 20.5115 | 56.8757 | 56.8757 | 57.1905 | 57.1905 | 57.1905 | 56.8757 | 56.8757 | 45.3479 | 45.3479 | 45.1157 | 45.1157 | 45.1157 | 45.3479 | 45.3479 | 54.349 | 45 | 65 | 45.4148 | 54.349 | 45
A-05 | -5686.511 | 13330.563 | -6993.4739 | -650.5781 | 60.8312 | 45.0024 | 61.3735 | 44.6964 | 60.9303 | 45.0391 | 53.1236 | 45 | 65 | 45.9563 | 54.9907 | 45 | 5.1322 | -11.4191 | 6.2869 | 10 | -10 | 10 | -53.7516 | -70.1799 | -45.5272 | 10 | -10 | 10 | -5.1322 | 6.2869 | 5.1322 | -11.4191 | 6.2869 | 5.1322 | -6.2869 | 8.2142 | -12.3263 | -53.7516 | -70.1799 | -45.5272 | -8.2142 | 12.3263 | 60.8312 | 60.8312 | 61.3735 | 61.3735 | 61.3735 | 60.9303 | 60.9303 | 45.0024 | 45.0024 | 44.6964 | 44.6399 | 44.7425 | 45.0391 | 45.0391 | 53.1236 | 45 | 65 | 45.9563 | 54.9907 | 45
A-06 | -6004.4393 | 13573.3814 | -6950.0945 | -618.8477 | 56.3612 | 45.2187 | 56.689 | 45.3685 | 56.4212 | 45.8928 | 53.5778 | 45 | 65 | 45.6095 | 54.9287 | 45 | 7.6983 | -17.1286 | 9.4303 | 10 | -10 | 10 | -120.941 | -157.9048 | -102.4363 | 10 | -10 | 10 | -7.6983 | 9.4303 | 7.6983 | -17.1286 | 9.4303 | 7.6983 | -9.4303 | 18.4819 | -27.7343 | -120.941 | -157.9048 | -102.4363 | -18.4819 | 27.7343 | 56.3612 | 56.3612 | 56.6891 | 56.6891 | 56.689 | 56.4212 | 56.4212 | 45.2187 | 45.2187 | 45.3685 | 44.975 | 45.6897 | 45.8928 | 45.8928 | 53.5778 | 45 | 65 | 45.6095 | 54.9287 | 45
A-07 | -6411.9602 | 13470.3577 | -6411.9602 | -646.4372 | 60.3667 | 45.0198 | 60.8282 | 44.7077 | 60.3667 | 45.0198 | 54.1599 | 45 | 65 | 45.7566 | 54.1599 | 45 | 5.9686 | -11.9373 | 5.9686 | 10 | -10 | 10 | -41.0344 | -63.2542 | -41.0344 | 10 | -10 | 10 | -5.9686 | 5.9686 | 5.9686 | -11.9373 | 5.9686 | 5.9686 | -5.9686 | 11.1099 | -11.1099 | -41.0344 | -63.2542 | -41.0344 | -11.1099 | 11.1099 | 60.3667 | 60.3667 | 60.8282 | 60.8282 | 60.8282 | 60.3667 | 60.3667 | 45.0198 | 45.0198 | 44.7077 | 44.7077 | 44.7077 | 45.0198 | 45.0198 | 54.1599 | 45 | 65 | 45.7566 | 54.1599 | 45
A-08 | -6950.0912 | 13573.3754 | -6004.4366 | -618.8476 | 56.4212 | 45.8928 | 56.689 | 45.3685 | 56.3612 | 45.2187 | 54.9287 | 45 | 65 | 45.6095 | 53.5778 | 45 | 9.4303 | -17.1286 | 7.6983 | 10 | -10 | 10 | -102.4363 | -157.9048 | -120.941 | 10 | -10 | 10 | -9.4303 | 7.6983 | 9.4303 | -17.1286 | 7.6983 | 9.4303 | -7.6983 | 27.7343 | -18.4819 | -102.4363 | -157.9048 | -120.941 | -27.7343 | 18.4819 | 56.4212 | 56.4212 | 56.689 | 56.689 | 56.689 | 56.3612 | 56.3612 | 45.8928 | 45.8928 | 45.3685 | 45.6897 | 44.975 | 45.2187 | 45.2187 | 54.9287 | 45 | 65 | 45.6095 | 53.5778 | 45
A-09 | -9424.7702 | 13561.2089 | -3520.3995 | -616.0392 | 55.9624 | 40.9238 | 56.2416 | 45.4221 | 55.9624 | 50.3451 | 53.464 | 40 | 65 | 45.6268 | 55.0291 | 50 | 8.9529 | -17.9059 | 8.9529 | 10 | -10 | 10 | -92.3274 | -142.322 | -92.3274 | 10 | -10 | 10 | -8.9529 | 8.9529 | 8.9529 | -17.9059 | 8.9529 | 8.9529 | -8.9529 | 24.9973 | -24.9973 | -92.3274 | -142.322 | -92.3274 | -24.9973 | 24.9973 | 55.9624 | 55.9624 | 56.2416 | 56.2416 | 56.2416 | 55.9624 | 55.9624 | 40.9238 | 40.9238 | 45.4221 | 40.7412 | 50.1031 | 50.3451 | 50.3451 | 53.464 | 40 | 65 | 45.6268 | 55.0291 | 50
A-10 | -10520.6523 | 21184.1186 | -10000.4101 | -663.0562 | 61.9373 | 45.1501 | 62.2545 | 45.3533 | 61.9373 | 45.9802 | 55.0197 | 45 | 65 | 49.8685 | 59.2863 | 45 | 8.9529 | -17.9059 | 8.9529 | 15 | -20 | 10 | -92.3274 | -142.322 | -92.3274 | 15 | -20 | 10 | -8.9529 | 8.9529 | 8.9529 | -17.9059 | 8.9529 | 8.9529 | -8.9529 | 24.9973 | -24.9973 | -92.3274 | -142.322 | -92.3274 | -24.9973 | 24.9973 | 61.9373 | 61.9373 | 62.2545 | 62.2545 | 62.2545 | 61.9373 | 61.9373 | 45.1501 | 45.1501 | 45.3533 | 44.9409 | 45.7657 | 45.9802 | 45.9802 | 55.0197 | 45 | 65 | 49.8685 | 59.2863 | 45
ProsNet results:

## Case_B
Case B |  | radial, 2 producers, 1 consumer in center, equally dimensioned pumps (quadratic)
pump1 | type: NMT PLUS ER 25/40-180 |  |  | n_nom: 4100 |  | dotV_max: 55.33 l/min |  | Deltap_max: 402.21 hPa
for B-9: |  | T_1_sec_h = 50 °C |  | T_2_sec_c = 40 °C
for B-10: |  | dotV_1_sec = -20 l/min |  | dotV_2_sec = 15 l/min
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim | dotV_1 | dotV_2 | dotV_3 | dotV_1h_2h | dotV_2h_3h | dotV_1h_1c | dotV_2h_2c | dotV_3h_3c | dotV_1c_2c | dotV_2c_3c | Deltap_1h_2h | Deltap_2h_3h | Deltap_1h_1c | Deltap_2h_2c | Deltap_3h_3c | Deltap_1c_2c | Deltap_2c_3c | T_1h_2h | T_1h_1c | T_2h_1h | T_2h_3h | T_2h_2c | T_3h_2h | T_3h_3c | T_1c_1h | T_1c_2c | T_2c_2h | T_2c_1c | T_2c_3c | T_3c_3h | T_3c_2c | T_PSM1h | T_PSM1c | T_PSM2h | T_PSM2c | T_PSM3h | T_PSM3c
B-01 | 7015.4021 | -13299.4516 | 7015.4021 | -731.3526 | 64.7934 | 51.4174 | 64.3956 | 51.7168 | 64.7934 | 51.4174 | 65 | 54.978 | 63.9992 | 45 | 65 | 54.978 | -7.4925 | 14.9851 | -7.4925 | -10 | 10 | -10 | -293.6664 | -258.6519 | -293.6664 | -10 | 10 | -10 | 7.4925 | -7.4925 | -7.4925 | 14.9851 | -7.4925 | -7.4925 | 7.4925 | -17.5073 | 17.5073 | -293.6664 | -258.6519 | -293.6664 | 17.5073 | -17.5073 | 64.7934 | 64.7934 | 64.3956 | 64.3956 | 64.3956 | 64.7934 | 64.7934 | 51.4174 | 51.4174 | 51.7168 | 51.7168 | 51.7168 | 51.4174 | 51.4174 | 65 | 54.978 | 63.9992 | 45 | 65 | 54.978
B-02 | 5516.3638 | -10351.6679 | 5516.3637 | -681.0596 | 65 | 44.9649 | 64.2417 | 45.4434 | 65 | 44.9649 | 65 | 57.1195 | 59.7881 | 45 | 65 | 57.1195 | -3.9334 | 7.8667 | -3.9334 | -10 | 10 | -10 | -135.9424 | -126.2926 | -135.9424 | -10 | 10 | -10 | 3.9334 | -3.9334 | -3.9334 | 7.8667 | -3.9334 | -3.9334 | 3.9334 | -4.8249 | 4.8249 | -135.9424 | -126.2926 | -135.9424 | 4.8249 | -4.8249 | 65 | 65 | 64.2417 | 64.2417 | 64.2417 | 65 | 65 | 44.9649 | 44.9649 | 45.4434 | 45.4434 | 45.4434 | 44.9649 | 44.9649 | 65 | 57.1195 | 59.7881 | 45 | 65 | 57.1195
B-04 | 6417.7794 | -12151.7214 | 6417.7794 | -694.6752 | 64.9982 | 46.6434 | 64.4002 | 47.0387 | 64.9982 | 46.6434 | 65 | 55.8317 | 62.3596 | 45 | 65 | 55.8317 | -4.995 | 9.99 | -4.995 | -10 | 10 | -10 | -130.5184 | -114.9564 | -130.5184 | -10 | 10 | -10 | 4.995 | -4.995 | -4.995 | 9.99 | -4.995 | -4.995 | 4.995 | -7.781 | 7.781 | -130.5184 | -114.9564 | -130.5184 | 7.781 | -7.781 | 64.9982 | 64.9982 | 64.4002 | 64.4002 | 64.4002 | 64.9982 | 64.9982 | 46.6434 | 46.6434 | 47.0387 | 47.0387 | 47.0387 | 46.6434 | 46.6434 | 65 | 55.8317 | 62.3596 | 45 | 65 | 55.8317
B-07 | 6801.5203 | -12893.4631 | 6801.5202 | -709.5774 | 64.9817 | 48.5132 | 64.4751 | 48.8657 | 64.9817 | 48.5132 | 65 | 55.2835 | 63.4192 | 45 | 65 | 55.2835 | -5.9 | 11.8001 | -5.9 | -10 | 10 | -10 | -305.8705 | -284.1583 | -305.8705 | -10 | 10 | -10 | 5.9 | -5.9 | -5.9 | 11.8001 | -5.9 | -5.9 | 5.9 | -10.8561 | 10.8561 | -305.8705 | -284.1583 | -305.8705 | 10.8561 | -10.8561 | 64.9817 | 64.9817 | 64.4751 | 64.4751 | 64.4751 | 64.9817 | 64.9817 | 48.5132 | 48.5132 | 48.8657 | 48.8657 | 48.8657 | 48.5132 | 48.5132 | 65 | 55.2835 | 63.4192 | 45 | 65 | 55.2835
B-09 | 2260.1214 | -11641.6342 | 10007.6309 | -626.1181 | 49.9335 | 45.6242 | 56.9778 | 45.8795 | 64.7053 | 45.6242 | 50 | 46.7713 | 56.6309 | 40 | 65 | 50.7034 | -7.4925 | 14.9851 | -7.4925 | -10 | 10 | -10 | -293.6664 | -258.6519 | -293.6664 | -10 | 10 | -10 | 7.4925 | -7.4925 | -7.4925 | 14.9851 | -7.4925 | -7.4925 | 7.4925 | -17.5073 | 17.5073 | -293.6664 | -258.6519 | -293.6664 | 17.5073 | -17.5073 | 49.9335 | 49.9335 | 49.6476 | 64.3081 | 56.9778 | 64.7053 | 64.7053 | 45.6242 | 45.6242 | 45.8795 | 45.8795 | 45.8795 | 45.6242 | 45.6242 | 50 | 46.7713 | 56.6309 | 40 | 65 | 50.7034
B-10 | 9097.8664 | -17374.8678 | 8964.1315 | -701.8528 | 64.991 | 47.6445 | 64.4651 | 47.9152 | 64.7361 | 47.6445 | 65 | 58.5015 | 61.5475 | 45 | 65 | 52.1941 | -7.4925 | 14.9851 | -7.4925 | -20 | 15 | -10 | -293.6664 | -258.6519 | -293.6664 | -20 | 15 | -10 | 7.4925 | -7.4925 | -7.4925 | 14.9851 | -7.4925 | -7.4925 | 7.4925 | -17.5073 | 17.5073 | -293.6664 | -258.6519 | -293.6664 | 17.5073 | -17.5073 | 64.991 | 64.991 | 64.5917 | 64.3386 | 64.4651 | 64.7361 | 64.7361 | 47.6445 | 47.6445 | 47.9152 | 47.9152 | 47.9152 | 47.6445 | 47.6445 | 65 | 58.5015 | 61.5475 | 45 | 65 | 52.1941
ProsNet results:

## Case_C
Case C |  | radial, 2 consumers, 1 producer at edge, pump (quadratic)
pump1 | type: NMT PLUS ER 25/40-180 |  |  | n_nom: 4100 |  | dotV_max: 55.33 l/min |  | Deltap_max: 402.21 hPa
for C-9: |  | T_1_sec_h = 50 °C |  | T_2_sec_c = 40 °C
for C-10: |  | dotV_1_sec = -20 l/min |  | dotV_2_sec = 15 l/min
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim | dotV_1 | dotV_2 | dotV_3 | dotV_1h_2h | dotV_2h_3h | dotV_1h_1c | dotV_2h_2c | dotV_3h_3c | dotV_1c_2c | dotV_2c_3c | Deltap_1h_2h | Deltap_2h_3h | Deltap_1h_1c | Deltap_2h_2c | Deltap_3h_3c | Deltap_1c_2c | Deltap_2c_3c | T_1h_2h | T_1h_1c | T_2h_1h | T_2h_3h | T_2h_2c | T_3h_2h | T_3h_3c | T_1c_1h | T_1c_2c | T_2c_2h | T_2c_1c | T_2c_3c | T_3c_3h | T_3c_2c | T_PSM1h | T_PSM1c | T_PSM2h | T_PSM2c | T_PSM3h | T_PSM3c
C-01 | 13700.1008 | -7261.9711 | -5809.7535 | -628.3762 | 58.4586 | 44.9619 | 58.2774 | 45.361 | 57.8737 | 45.044 | 65 | 45.4284 | 55.3742 | 45 | 53.2996 | 45 | -14.501 | 8.0319 | 6.4691 | -10 | 10 | 10 | -205.4628 | -74.3073 | -48.2048 | -10 | 10 | 10 | 14.501 | 6.4691 | -14.501 | 8.0319 | 6.4691 | -14.501 | -6.4691 | -65.5778 | -13.0513 | -205.4628 | -74.3073 | -48.2048 | 65.5778 | 13.0513 | 58.4586 | 58.4586 | 58.2774 | 58.2774 | 58.2774 | 57.8737 | 57.8737 | 44.9619 | 44.9619 | 45.361 | 45.091 | 44.7558 | 45.044 | 45.044 | 65 | 45.4284 | 55.3742 | 45 | 53.2996 | 45
C-02 | 12113.6301 | -6212.1876 | -5234.2413 | -667.2012 | 63.7568 | 44.5895 | 63.4329 | 45.001 | 62.7456 | 45.0001 | 65 | 47.6948 | 53.8746 | 45 | 52.4775 | 45 | -9.0285 | 4.8148 | 4.2137 | -10 | 10 | 10 | -98.151 | -47.3089 | -36.2344 | -10 | 10 | 10 | 9.0285 | 4.2137 | -9.0285 | 4.8148 | 4.2137 | -9.0285 | -4.2137 | -25.4211 | -5.5372 | -98.151 | -47.3089 | -36.2344 | 25.4211 | 5.5372 | 63.7568 | 63.7568 | 63.4329 | 63.4329 | 63.4329 | 62.7456 | 62.7456 | 44.5895 | 44.5895 | 45.001 | 44.7948 | 44.5591 | 45.0001 | 45.0001 | 65 | 47.6948 | 53.8746 | 45 | 52.4775 | 45
C-03 | 13690.5086 | -7034.4386 | -6022.0129 | -634.0571 | 59.2641 | 44.8226 | 59.0667 | 45.1524 | 58.6465 | 45.0356 | 65 | 45.4421 | 55.0492 | 45 | 53.6029 | 45 | -13.5428 | 7.2222 | 6.3206 | -10 | 10 | 10 | -220.8398 | -106.445 | -81.5274 | -10 | 10 | 10 | 13.5428 | 6.3206 | -13.5428 | 7.2222 | 6.3206 | -13.5428 | -6.3206 | -57.1974 | -12.4588 | -220.8398 | -106.445 | -81.5274 | 57.1974 | 12.4588 | 59.2641 | 59.2641 | 59.0667 | 59.0667 | 59.0667 | 58.6465 | 58.6465 | 44.8226 | 44.8226 | 45.1524 | 44.9602 | 44.7407 | 45.0356 | 45.0356 | 65 | 45.4421 | 55.0492 | 45 | 53.6029 | 45
C-04 | 12430.7447 | -7218.3106 | -4548.36 | -664.0742 | 63.3718 | 44.616 | 63.0652 | 45.0131 | 62.3003 | 45 | 65 | 47.2418 | 55.3119 | 45 | 51.4977 | 45 | -9.4681 | 5.7123 | 3.7558 | -10 | 10 | 10 | -93.4985 | -37.5852 | -28.7869 | -10 | 10 | 10 | 9.4681 | 3.7558 | -9.4681 | 5.7123 | 3.7558 | -9.4681 | -3.7558 | -27.9567 | -4.3991 | -93.4985 | -37.5852 | -28.7869 | 27.9567 | 4.3991 | 63.3718 | 63.3718 | 63.0652 | 63.0652 | 63.0652 | 62.3003 | 62.3003 | 44.616 | 44.616 | 45.0131 | 44.8118 | 44.5057 | 45 | 45 | 65 | 47.2418 | 55.3119 | 45 | 51.4977 | 45
C-05 | 12324.0583 | -5724.0134 | -5934.3601 | -665.6848 | 63.5164 | 44.6017 | 63.2037 | 45.0003 | 62.6046 | 45.001 | 65 | 47.3942 | 53.1772 | 45 | 53.4777 | 45 | -9.308 | 4.4921 | 4.8159 | -10 | 10 | 10 | -95.2187 | -41.1803 | -26.7146 | -10 | 10 | 10 | 9.308 | 4.8159 | -9.308 | 4.4921 | 4.8159 | -9.308 | -4.8159 | -27.0192 | -7.2329 | -95.2187 | -41.1803 | -26.7146 | 27.0192 | 7.2329 | 63.5164 | 63.5164 | 63.2037 | 63.2037 | 63.2037 | 62.6046 | 62.6046 | 44.6017 | 44.6017 | 45.0003 | 44.8008 | 44.6148 | 45.001 | 45.001 | 65 | 47.3942 | 53.1772 | 45 | 53.4777 | 45
C-06 | 12563.3121 | -6701.6668 | -5198.6861 | -662.9592 | 63.1841 | 44.6189 | 62.8849 | 45.0052 | 62.2205 | 45.0001 | 65 | 47.0524 | 54.5738 | 45 | 52.4267 | 45 | -9.6673 | 5.3546 | 4.3127 | -10 | 10 | 10 | -91.3168 | -33.0255 | -21.4243 | -10 | 10 | 10 | 9.6673 | 4.3127 | -9.6673 | 5.3546 | 4.3127 | -9.6673 | -4.3127 | -29.1457 | -5.8006 | -91.3168 | -33.0255 | -21.4243 | 29.1457 | 5.8006 | 63.1841 | 63.1841 | 62.8849 | 62.8849 | 62.8849 | 62.2205 | 62.2205 | 44.6189 | 44.6189 | 45.0052 | 44.8107 | 44.5692 | 45.0001 | 45.0001 | 65 | 47.0524 | 54.5738 | 45 | 52.4267 | 45
C-07 | 13727.4382 | -6426.5167 | -6669.1154 | -631.8061 | 58.8885 | 44.8427 | 58.6985 | 45.0735 | 58.3335 | 45.1447 | 65 | 45.3894 | 54.1807 | 45 | 54.5273 | 45 | -13.962 | 6.7382 | 7.2238 | -10 | 10 | 10 | -214.242 | -92.6557 | -60.1078 | -10 | 10 | 10 | 13.962 | 7.2238 | -13.962 | 6.7382 | 7.2238 | -13.962 | -7.2238 | -60.7932 | -16.274 | -214.242 | -92.6557 | -60.1078 | 60.7932 | 16.274 | 58.8885 | 58.8885 | 58.6985 | 58.6985 | 58.6985 | 58.3335 | 58.3335 | 44.8427 | 44.8427 | 45.0735 | 44.9763 | 44.8857 | 45.1447 | 45.1447 | 65 | 45.3894 | 54.1807 | 45 | 54.5273 | 45
C-08 | 13579.8786 | -7784.4976 | -5164.4852 | -630.8958 | 58.7562 | 45.0964 | 58.5699 | 45.5912 | 58.1037 | 45.0078 | 65 | 45.6002 | 56.1207 | 45 | 52.3778 | 45 | -14.2021 | 8.5684 | 5.6337 | -10 | 10 | 10 | -210.3717 | -84.5667 | -64.7706 | -10 | 10 | 10 | 14.2021 | 5.6337 | -14.2021 | 8.5684 | 5.6337 | -14.2021 | -5.6337 | -62.9025 | -9.8981 | -210.3717 | -84.5667 | -64.7706 | 62.9025 | 9.8981 | 58.7562 | 58.7562 | 58.5699 | 58.5699 | 58.5699 | 58.1037 | 58.1037 | 45.0964 | 45.0964 | 45.5912 | 45.2287 | 44.6774 | 45.0078 | 45.0078 | 65 | 45.6002 | 56.1207 | 45 | 52.3778 | 45
C-09 | 5403.3525 | -3982.7763 | -890.8876 | -529.6886 | 47.4201 | 42.0969 | 47.2819 | 40.198 | 46.9741 | 45.0068 | 50 | 42.2809 | 45.6897 | 40 | 46.2727 | 45 | -14.501 | 8.0319 | 6.4691 | -10 | 10 | 10 | -205.4628 | -74.3073 | -48.2048 | -10 | 10 | 10 | 14.501 | 6.4691 | -14.501 | 8.0319 | 6.4691 | -14.501 | -6.4691 | -65.5778 | -13.0513 | -205.4628 | -74.3073 | -48.2048 | 65.5778 | 13.0513 | 47.4201 | 47.4201 | 47.2819 | 47.2819 | 47.2819 | 46.9741 | 46.9741 | 42.0969 | 42.0969 | 40.198 | 42.2148 | 44.7188 | 45.0068 | 45.0068 | 50 | 42.2809 | 45.6897 | 40 | 46.2727 | 45
C-10 | 19186.1686 | -10368.611 | -8148.3006 | -669.257 | 63.7066 | 44.8053 | 63.5049 | 45.063 | 63.0556 | 45.0618 | 65 | 51.2956 | 54.8749 | 45 | 56.6404 | 45 | -14.501 | 8.0319 | 6.4691 | -20 | 15 | 10 | -205.4628 | -74.3073 | -48.2048 | -20 | 15 | 10 | 14.501 | 6.4691 | -14.501 | 8.0319 | 6.4691 | -14.501 | -6.4691 | -65.5778 | -13.0513 | -205.4628 | -74.3073 | -48.2048 | 65.5778 | 13.0513 | 63.7066 | 63.7066 | 63.5049 | 63.5049 | 63.5049 | 63.0556 | 63.0556 | 44.8053 | 44.8053 | 45.063 | 44.9338 | 44.7733 | 45.0618 | 45.0618 | 65 | 51.2956 | 54.8749 | 45 | 56.6404 | 45
ProsNet results:

## Case_D
Case D |  | radial, 2 producers, 1 consumer at edge, equally dimensioned pumps (quadratic)
pump1 | type: NMT PLUS ER 25/40-180 |  |  | n_nom: 4100 |  | dotV_max: 55.33 l/min |  | Deltap_max: 402.21 hPa
for D-9: |  | T_1_sec_c = 40 °C |  | T_2_sec_h = 50 °C
for D-10: |  | dotV_1_sec = 15 l/min |  | dotV_2_sec = -20 l/min
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim | dotV_1 | dotV_2 | dotV_3 | dotV_1h_2h | dotV_2h_3h | dotV_1h_1c | dotV_2h_2c | dotV_3h_3c | dotV_1c_2c | dotV_2c_3c | Deltap_1h_2h | Deltap_2h_3h | Deltap_1h_1c | Deltap_2h_2c | Deltap_3h_3c | Deltap_1c_2c | Deltap_2c_3c | T_1h_2h | T_1h_1c | T_2h_1h | T_2h_3h | T_2h_2c | T_3h_2h | T_3h_3c | T_1c_1h | T_1c_2c | T_2c_2h | T_2c_1c | T_2c_3c | T_3c_3h | T_3c_2c | T_PSM1h | T_PSM1c | T_PSM2h | T_PSM2c | T_PSM3h | T_PSM3c
D-01 | -13047.6133 | 7992.0269 | 5771.7126 | -716.1262 | 64.3799 | 49.8653 | 64.7389 | 49.6985 | 64.9966 | 49.2937 | 63.6394 | 45 | 65 | 53.5828 | 65 | 56.7547 | 12.8418 | -7.591 | -5.2508 | 10 | -10 | -10 | -189.9563 | -292.8163 | -310.0131 | 10 | -10 | -10 | -12.8418 | -5.2508 | 12.8418 | -7.591 | -5.2508 | 12.8418 | 5.2508 | 51.43 | 8.5984 | -189.9563 | -292.8163 | -310.0131 | -51.43 | -8.5984 | 64.3799 | 64.3799 | 64.6116 | 64.4276 | 64.7389 | 64.9966 | 64.9966 | 49.8653 | 49.8653 | 49.6985 | 49.6985 | 49.6985 | 49.2937 | 49.2937 | 63.6394 | 45 | 65 | 53.5828 | 65 | 56.7547
D-02 | -9448.9044 | 5908.8321 | 4216.5875 | -676.5151 | 64.164 | 45.1784 | 64.9999 | 44.9149 | 65 | 44.2794 | 58.4984 | 45 | 65 | 56.5588 | 65 | 58.9763 | 7.1098 | -4.2027 | -2.9071 | 10 | -10 | -10 | -103.1593 | -134.6883 | -139.9596 | 10 | -10 | -10 | -7.1098 | -2.9071 | 7.1098 | -4.2027 | -2.9071 | 7.1098 | 2.9071 | 15.7645 | 2.6356 | -103.1593 | -134.6883 | -139.9596 | -15.7645 | -2.6356 | 64.164 | 64.164 | 64.5815 | 63.9766 | 64.9999 | 65 | 65 | 45.1784 | 45.1784 | 44.9149 | 44.9149 | 44.9149 | 44.2794 | 44.2794 | 58.4984 | 45 | 65 | 56.5588 | 65 | 58.9763
D-03 | -11066.9465 | 6866.9875 | 4882.8812 | -682.9222 | 64.3031 | 45.8362 | 64.9976 | 45.6129 | 65 | 45.073 | 60.8099 | 45 | 65 | 55.19 | 65 | 58.0245 | 8.5612 | -5.0607 | -3.5006 | 10 | -10 | -10 | -84.425 | -130.1406 | -137.7836 | 10 | -10 | -10 | -8.5612 | -3.5006 | 8.5612 | -5.0607 | -3.5006 | 8.5612 | 3.5006 | 22.8578 | 3.8215 | -84.425 | -130.1406 | -137.7836 | -22.8578 | -3.8215 | 64.3031 | 64.3031 | 64.6505 | 64.1487 | 64.9976 | 65 | 65 | 45.8362 | 45.8362 | 45.6129 | 45.6129 | 45.6129 | 45.073 | 45.073 | 60.8099 | 45 | 65 | 55.19 | 65 | 58.0245
D-06 | -12478.1163 | 7698.3235 | 5478.5082 | -698.7154 | 64.4146 | 47.6998 | 64.9557 | 47.5106 | 64.9998 | 47.052 | 62.8259 | 45 | 65 | 54.0024 | 65 | 57.1736 | 10.6648 | -6.3041 | -4.3606 | 10 | -10 | -10 | -232.1084 | -303.0488 | -314.909 | 10 | -10 | -10 | -10.6648 | -4.3606 | 10.6648 | -6.3041 | -4.3606 | 10.6648 | 4.3606 | 35.4702 | 5.9301 | -232.1084 | -303.0488 | -314.909 | -35.4702 | -5.9301 | 64.4146 | 64.4146 | 64.6939 | 64.3154 | 64.9557 | 64.9998 | 64.9998 | 47.6998 | 47.6998 | 47.5106 | 47.5106 | 47.5106 | 47.052 | 47.052 | 62.8259 | 45 | 65 | 54.0024 | 65 | 57.1736
D-09 | -10531.7072 | 3245.3288 | 7920.9159 | -634.5375 | 55.643 | 43.9271 | 49.894 | 43.7865 | 64.9953 | 43.4452 | 55.0453 | 40 | 50 | 45.3638 | 65 | 53.6844 | 12.8418 | -7.591 | -5.2508 | 10 | -10 | -10 | -189.9563 | -292.8163 | -310.0131 | 10 | -10 | -10 | -12.8418 | -5.2508 | 12.8418 | -7.591 | -5.2508 | 12.8418 | 5.2508 | 51.43 | 8.5984 | -189.9563 | -292.8163 | -310.0131 | -51.43 | -8.5984 | 55.643 | 55.643 | 55.836 | 64.4263 | 49.894 | 64.9953 | 64.9953 | 43.9271 | 43.9271 | 43.7865 | 43.7865 | 43.7865 | 43.4452 | 43.4452 | 55.0453 | 40 | 50 | 45.3638 | 65 | 53.6844
D-10 | -16099.8659 | 9843.4963 | 6947.4526 | -691.083 | 64.5268 | 46.6168 | 64.989 | 46.4643 | 64.9959 | 46.0943 | 60.3332 | 45 | 65 | 57.9689 | 65 | 55.0751 | 12.8418 | -7.591 | -5.2508 | 15 | -20 | -10 | -189.9563 | -292.8163 | -310.0131 | 15 | -20 | -10 | -12.8418 | -5.2508 | 12.8418 | -7.591 | -5.2508 | 12.8418 | 5.2508 | 51.43 | 8.5984 | -189.9563 | -292.8163 | -310.0131 | -51.43 | -8.5984 | 64.5268 | 64.5268 | 64.7592 | 64.4269 | 64.989 | 64.9959 | 64.9959 | 46.6168 | 46.6168 | 46.4643 | 46.4643 | 46.4643 | 46.0943 | 46.0943 | 60.3332 | 45 | 65 | 57.9689 | 65 | 55.0751
ProsNet results:

## Case_E
Case E |  | meshed, 2 consumers, 1 producer, pump (quadratic)
pump1 | type: NMT PLUS ER 25/40-180 |  |  | n_nom: 4100 |  | dotV_max: 55.33 l/min |  | Deltap_max: 402.21 hPa
for E-9: |  | T_1_sec_c = 40 °C |  | T_3_sec_c = 50 °C
for E-10: |  | dotV_1_sec = 15 l/min |  | dotV_2_sec = -20 l/min
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim | dotV_1 | dotV_2 | dotV_3 | dotV_1h_2h | dotV_1h_3h | dotV_2h_3h | dotV_1h_1c | dotV_2h_2c | dotV_3h_3c | dotV_1c_2c | dotV_1c_3c | dotV_2c_3c | Deltap_1h_2h | Deltap_1h_3h | Deltap_2h_3h | Deltap_1h_1c | Deltap_2h_2c | Deltap_3h_3c | Deltap_1c_2c | Deltap_1c_3c | Deltap_2c_3c | T_1h_2h | T_1h_3h | T_1h_1c | T_2h_1h | T_2h_3h | T_2h_2c | T_3h_1h | T_3h_2h | T_3h_3c | T_1c_1h | T_1c_2c | T_1c_3c | T_2c_2h | T_2c_1c | T_2c_3c | T_3c_3h | T_3c_1c | T_3c_2c | T_PSM1h | T_PSM1c | T_PSM2h | T_PSM2c | T_PSM3h | T_PSM3c
E-01 | -6472.5846 | 13561.2083 | -6472.5846 | -616.0392 | 55.9624 | 45.6344 | 56.2416 | 45.4221 | 55.9624 | 45.6344 | 54.2465 | 45 | 65 | 45.6268 | 54.2465 | 45 | 8.9529 | -17.9059 | 8.9529 | 10 | -10 | 10 | -92.3274 | -142.322 | -92.3274 | 10 | -10 | 10 | -8.9529 | 0 | 8.9529 | 8.9529 | -17.9059 | 8.9529 | 8.9529 | 4.1811e-10 | -8.9529 | 24.9973 | 0 | -24.9973 | -92.3274 | -142.322 | -92.3274 | -24.9973 | 0 | 24.9973 | 55.9624 | 1.85 | 55.9624 | 56.2416 | 56.2416 | 56.2416 | 1.85 | 55.9624 | 55.9624 | 45.6344 | 45.6344 | 45.6344 | 45.4221 | 45.4221 | 45.4221 | 45.6344 | 12 | 45.6344 | 54.2465 | 45 | 65 | 45.6268 | 54.2465 | 45
E-02 | -6239.7026 | 13134.772 | -6239.7026 | -655.3669 | 61.4924 | 45.0055 | 62.014 | 44.6613 | 61.4924 | 45.0055 | 53.9139 | 45 | 65 | 46.236 | 53.9139 | 45 | 5.4066 | -10.8133 | 5.4066 | 10 | -10 | 10 | -59.6544 | -77.8869 | -59.6544 | 10 | -10 | 10 | -5.4066 | 0 | 5.4066 | 5.4066 | -10.8133 | 5.4066 | 5.4066 | 0 | -5.4066 | 9.1162 | 0 | -9.1162 | -59.6544 | -77.8869 | -59.6544 | -9.1162 | 0 | 9.1162 | 61.4924 | 1.85 | 61.4924 | 62.014 | 62.014 | 62.014 | 1.85 | 61.4924 | 61.4924 | 45.0055 | 45.0055 | 1.85 | 44.6613 | 44.6613 | 44.6613 | 45.0055 | 1.85 | 45.0055 | 53.9139 | 45 | 65 | 46.236 | 53.9139 | 45
E-03 | -7020.0356 | 13435.8122 | -5453.4788 | -962.2978 | 60.4189 | 45.0585 | 61.3117 | 44.5523 | 60.8238 | 45.0012 | 55.0286 | 45 | 65 | 45.806 | 52.7907 | 45 | 6.5289 | -11.4527 | 4.9238 | 10 | -10 | 10 | -49.0994 | -69.7402 | -49.4752 | 10 | -10 | 10 | -5.7526 | -0.77624 | 5.7 | 6.5289 | -11.4527 | 4.9238 | 5.7526 | 0.77624 | -5.7 | 10.3204 | 0.18791 | -10.1325 | -49.0994 | -69.7402 | -49.4752 | -10.3204 | -0.18791 | 10.1325 | 60.8282 | 57.3856 | 60.4189 | 61.3117 | 61.3117 | 61.3117 | 60.8238 | 60.8238 | 60.8238 | 45.0585 | 45.0585 | 45.0585 | 44.5523 | 44.7344 | 44.3685 | 45.0012 | 42.7305 | 44.692 | 55.0286 | 45 | 65 | 45.806 | 52.7907 | 45
E-04 | -6544.29 | 13709.6553 | -6544.29 | -621.0753 | 56.8757 | 45.3479 | 57.1905 | 45.1157 | 56.8757 | 45.3479 | 54.349 | 45 | 65 | 45.4148 | 54.349 | 45 | 8.1099 | -16.2199 | 8.1099 | 10 | -10 | 10 | -134.2225 | -175.2455 | -134.2225 | 10 | -10 | 10 | -8.1099 | 0 | 8.1099 | 8.1099 | -16.2199 | 8.1099 | 8.1099 | 0 | -8.1099 | 20.5115 | 0 | -20.5115 | -134.2225 | -175.2455 | -134.2225 | -20.5115 | 0 | 20.5115 | 56.8757 | 1.85 | 56.8757 | 57.1905 | 57.1905 | 57.1905 | 1.85 | 56.8757 | 56.8757 | 45.3479 | 45.3479 | 1.85 | 45.1157 | 45.1157 | 45.1157 | 45.3479 | 1.85 | 45.3479 | 54.349 | 45 | 65 | 45.4148 | 54.349 | 45
E-05 | -5453.4788 | 13435.8122 | -7020.0356 | -962.2978 | 60.8238 | 45.0012 | 61.3117 | 44.5523 | 60.4189 | 45.0585 | 52.7907 | 45 | 65 | 45.806 | 55.0286 | 45 | 4.9238 | -11.4527 | 6.5289 | 10 | -10 | 10 | -49.4752 | -69.7402 | -49.0994 | 10 | -10 | 10 | -5.7 | 0.77624 | 5.7526 | 4.9238 | -11.4527 | 6.5289 | 5.7 | -0.77624 | -5.7526 | 10.1325 | -0.18791 | -10.3204 | -49.4752 | -69.7402 | -49.0994 | -10.1325 | 0.18791 | 10.3204 | 60.8238 | 60.8238 | 60.8238 | 61.3117 | 61.3117 | 61.3117 | 57.3856 | 60.8282 | 60.4189 | 45.0012 | 44.692 | 42.7305 | 44.5523 | 44.3685 | 44.7344 | 45.0585 | 45.0585 | 45.0585 | 52.7907 | 45 | 65 | 45.806 | 55.0286 | 45
E-06 | -5788.9371 | 13597.2382 | -6886.1499 | -922.1513 | 56.3488 | 45.1516 | 56.6438 | 45.3366 | 56.1006 | 46.0556 | 53.2699 | 45 | 65 | 45.5754 | 54.8374 | 45 | 7.3857 | -17.179 | 9.7933 | 10 | -10 | 10 | -111.3192 | -156.9154 | -110.4736 | 10 | -10 | 10 | -8.55 | 1.1644 | 8.629 | 7.3857 | -17.179 | 9.7933 | 8.55 | -1.1644 | -8.629 | 22.7981 | -0.4228 | -23.2209 | -111.3192 | -156.9154 | -110.4736 | -22.7981 | 0.4228 | 23.2209 | 56.3488 | 56.3488 | 56.3488 | 56.6438 | 56.6438 | 56.6438 | 54.2415 | 56.3515 | 56.1006 | 45.1516 | 45.0543 | 44.4375 | 45.3366 | 44.8359 | 45.8327 | 46.0556 | 46.0556 | 46.0556 | 53.2699 | 45 | 65 | 45.5754 | 54.8374 | 45
E-07 | -6411.9639 | 13470.365 | -6411.9639 | -646.4372 | 60.3667 | 45.0198 | 60.8282 | 44.7077 | 60.3667 | 45.0198 | 54.1599 | 45 | 65 | 45.7566 | 54.1599 | 45 | 5.9686 | -11.9373 | 5.9686 | 10 | -10 | 10 | -41.0344 | -63.2542 | -41.0344 | 10 | -10 | 10 | -5.9686 | 0 | 5.9686 | 5.9686 | -11.9373 | 5.9686 | 5.9686 | 2.5075e-09 | -5.9686 | 11.1099 | 0 | -11.1099 | -41.0344 | -63.2542 | -41.0344 | -11.1099 | 0 | 11.1099 | 60.3667 | 1.85 | 60.3667 | 60.8282 | 60.8282 | 60.8282 | 1.85 | 60.3667 | 60.3667 | 45.0198 | 45.0198 | 45.0198 | 44.7077 | 44.7077 | 44.7077 | 45.0198 | 12 | 45.0198 | 54.1599 | 45 | 65 | 45.7566 | 54.1599 | 45
E-08 | -6886.1499 | 13597.2382 | -5788.9371 | -922.1513 | 56.1006 | 46.0556 | 56.6438 | 45.3366 | 56.3488 | 45.1516 | 54.8374 | 45 | 65 | 45.5754 | 53.2699 | 45 | 9.7933 | -17.179 | 7.3857 | 10 | -10 | 10 | -110.4736 | -156.9154 | -111.3192 | 10 | -10 | 10 | -8.629 | -1.1644 | 8.55 | 9.7933 | -17.179 | 7.3857 | 8.629 | 1.1644 | -8.55 | 23.2209 | 0.4228 | -22.7981 | -110.4736 | -156.9154 | -111.3192 | -23.2209 | -0.4228 | 22.7981 | 56.3515 | 54.2415 | 56.1006 | 56.6438 | 56.6438 | 56.6438 | 56.3488 | 56.3488 | 56.3488 | 46.0556 | 46.0556 | 46.0556 | 45.3366 | 45.8327 | 44.8359 | 45.1516 | 44.4375 | 45.0543 | 54.8374 | 45 | 65 | 45.5754 | 53.2699 | 45
E-09 | -9424.7699 | 13561.2083 | -3520.3992 | -616.0392 | 55.9624 | 40.9238 | 56.2416 | 45.4221 | 55.9624 | 50.3451 | 53.464 | 40 | 65 | 45.6268 | 55.0291 | 50 | 8.9529 | -17.9059 | 8.9529 | 10 | -10 | 10 | -92.3274 | -142.322 | -92.3274 | 10 | -10 | 10 | -8.9529 | 0 | 8.9529 | 8.9529 | -17.9059 | 8.9529 | 8.9529 | 4.1811e-10 | -8.9529 | 24.9973 | 0 | -24.9973 | -92.3274 | -142.322 | -92.3274 | -24.9973 | 0 | 24.9973 | 55.9624 | 1.85 | 55.9624 | 56.2416 | 56.2416 | 56.2416 | 1.85 | 55.9624 | 55.9624 | 40.9238 | 40.9238 | 40.9238 | 45.4221 | 40.7412 | 50.103 | 50.3451 | 12 | 50.3451 | 53.464 | 40 | 65 | 45.6268 | 55.0291 | 50
E-10 | -10520.6519 | 21184.1178 | -10000.4097 | -663.0562 | 61.9373 | 45.1501 | 62.2545 | 45.3533 | 61.9373 | 45.9802 | 55.0197 | 45 | 65 | 49.8685 | 59.2863 | 45 | 8.9529 | -17.9059 | 8.9529 | 15 | -20 | 10 | -92.3274 | -142.322 | -92.3274 | 15 | -20 | 10 | -8.9529 | 0 | 8.9529 | 8.9529 | -17.9059 | 8.9529 | 8.9529 | 4.1811e-10 | -8.9529 | 24.9973 | 0 | -24.9973 | -92.3274 | -142.322 | -92.3274 | -24.9973 | 0 | 24.9973 | 61.9373 | 1.85 | 61.9373 | 62.2545 | 62.2545 | 62.2545 | 1.85 | 61.9373 | 61.9373 | 45.1501 | 45.1501 | 45.1501 | 45.3533 | 44.9409 | 45.7657 | 45.9802 | 12 | 45.9802 | 55.0197 | 45 | 65 | 49.8685 | 59.2863 | 45
ProsNet results:

## Case_F
Case F |  | meshed, 2 producers, 1 consumer, equally dimensioned pumps (quadratic)
pump1 | type: NMT PLUS ER 25/40-180 |  |  | n_nom: 4100 |  | dotV_max: 55.33 l/min |  | Deltap_max: 402.21 hPa
for F-9: |  | T_1_sec_h = 50 °C |  | T_2_sec_c = 40 °C
for F-10: |  | dotV_1_sec = -20 l/min |  | dotV_2_sec = 15 l/min
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim | dotV_1 | dotV_2 | dotV_3 | dotV_1h_2h | dotV_1h_3h | dotV_2h_3h | dotV_1h_1c | dotV_2h_2c | dotV_3h_3c | dotV_1c_2c | dotV_1c_3c | dotV_2c_3c | Deltap_1h_2h | Deltap_1h_3h | Deltap_2h_3h | Deltap_1h_1c | Deltap_2h_2c | Deltap_3h_3c | Deltap_1c_2c | Deltap_1c_3c | Deltap_2c_3c | T_1h_2h | T_1h_3h | T_1h_1c | T_2h_1h | T_2h_3h | T_2h_2c | T_3h_1h | T_3h_2h | T_3h_3c | T_1c_1h | T_1c_2c | T_1c_3c | T_2c_2h | T_2c_1c | T_2c_3c | T_3c_3h | T_3c_1c | T_3c_2c | T_PSM1h | T_PSM1c | T_PSM2h | T_PSM2c | T_PSM3h | T_PSM3c
F-01 | 7015.4021 | -13299.4516 | 7015.4021 | -731.3526 | 64.7934 | 51.4174 | 64.3956 | 51.7168 | 64.7934 | 51.4174 | 65 | 54.978 | 63.9992 | 45 | 65 | 54.978 | -7.4925 | 14.9851 | -7.4925 | -10 | 10 | -10 | -293.6664 | -258.6519 | -293.6664 | -10 | 10 | -10 | 7.4925 | 1.1333e-12 | -7.4925 | -7.4925 | 14.9851 | -7.4925 | -7.4925 | -1.3003e-12 | 7.4925 | -17.5073 | 0 | 17.5073 | -293.6664 | -258.6519 | -293.6664 | 17.5073 | 0 | -17.5073 | 64.7934 | 64.7934 | 64.7934 | 64.3956 | 64.3956 | 64.3956 | 12 | 64.7934 | 64.7934 | 51.4174 | 51.4174 | 12 | 51.7168 | 51.7168 | 51.7168 | 51.4174 | 51.4174 | 51.4174 | 65 | 54.978 | 63.9992 | 45 | 65 | 54.978
F-02 | 5516.3638 | -10351.668 | 5516.3638 | -681.0596 | 65 | 44.9649 | 64.2417 | 45.4434 | 65 | 44.9649 | 65 | 57.1195 | 59.7881 | 45 | 65 | 57.1195 | -3.9334 | 7.8667 | -3.9334 | -10 | 10 | -10 | -135.9424 | -126.2926 | -135.9424 | -10 | 10 | -10 | 3.9334 | -1.5572e-11 | -3.9334 | -3.9334 | 7.8667 | -3.9334 | -3.9334 | 0 | 3.9334 | -4.8249 | 0 | 4.8249 | -135.9424 | -126.2926 | -135.9424 | 4.8249 | 0 | -4.8249 | 65 | 12 | 65 | 64.2417 | 64.2417 | 64.2417 | 65 | 65 | 65 | 44.9649 | 44.9649 | 1.85 | 45.4434 | 45.4434 | 45.4434 | 44.9649 | 1.85 | 44.9649 | 65 | 57.1195 | 59.7881 | 45 | 65 | 57.1195
F-04 | 6417.7794 | -12151.7214 | 6417.7794 | -694.6752 | 64.9982 | 46.6434 | 64.4002 | 47.0387 | 64.9982 | 46.6434 | 65 | 55.8317 | 62.3596 | 45 | 65 | 55.8317 | -4.995 | 9.99 | -4.995 | -10 | 10 | -10 | -130.5184 | -114.9564 | -130.5184 | -10 | 10 | -10 | 4.995 | 0 | -4.995 | -4.995 | 9.99 | -4.995 | -4.995 | 0 | 4.995 | -7.781 | 0 | 7.781 | -130.5184 | -114.9564 | -130.5184 | 7.781 | 0 | -7.781 | 64.9982 | 1.85 | 64.9982 | 64.4002 | 64.4002 | 64.4002 | 1.85 | 64.9982 | 64.9982 | 46.6434 | 46.6434 | 1.85 | 47.0387 | 47.0387 | 47.0387 | 46.6434 | 1.85 | 46.6434 | 65 | 55.8317 | 62.3596 | 45 | 65 | 55.8317
F-07 | 6801.5202 | -12893.4631 | 6801.5202 | -709.5774 | 64.9817 | 48.5132 | 64.4751 | 48.8657 | 64.9817 | 48.5132 | 65 | 55.2835 | 63.4192 | 45 | 65 | 55.2835 | -5.9 | 11.8001 | -5.9 | -10 | 10 | -10 | -305.8705 | -284.1583 | -305.8705 | -10 | 10 | -10 | 5.9 | 0 | -5.9 | -5.9 | 11.8001 | -5.9 | -5.9 | 0 | 5.9 | -10.8561 | 0 | 10.8561 | -305.8705 | -284.1583 | -305.8705 | 10.8561 | 0 | -10.8561 | 64.9817 | 1.85 | 64.9817 | 64.4751 | 64.4751 | 64.4751 | 1.85 | 64.9817 | 64.9817 | 48.5132 | 48.5132 | 1.85 | 48.8657 | 48.8657 | 48.8657 | 48.5132 | 1.85 | 48.5132 | 65 | 55.2835 | 63.4192 | 45 | 65 | 55.2835
F-09 | 2260.1213 | -11641.6342 | 10007.631 | -626.1181 | 49.9335 | 45.6242 | 56.9778 | 45.8795 | 64.7053 | 45.6242 | 50 | 46.7713 | 56.6309 | 40 | 65 | 50.7034 | -7.4925 | 14.9851 | -7.4925 | -10 | 10 | -10 | -293.6664 | -258.6519 | -293.6664 | -10 | 10 | -10 | 7.4925 | 1.1333e-12 | -7.4925 | -7.4925 | 14.9851 | -7.4925 | -7.4925 | -1.3003e-12 | 7.4925 | -17.5073 | 0 | 17.5073 | -293.6664 | -258.6519 | -293.6664 | 17.5073 | 0 | -17.5073 | 49.9335 | 49.9335 | 49.9335 | 49.6476 | 64.3081 | 56.9778 | 12 | 64.7053 | 64.7053 | 45.6242 | 45.6242 | 12 | 45.8795 | 45.8795 | 45.8795 | 45.6242 | 45.6242 | 45.6242 | 50 | 46.7713 | 56.6309 | 40 | 65 | 50.7034
F-10 | 9097.8664 | -17374.8678 | 8964.1315 | -701.8528 | 64.991 | 47.6445 | 64.4651 | 47.9152 | 64.7361 | 47.6445 | 65 | 58.5015 | 61.5475 | 45 | 65 | 52.1941 | -7.4925 | 14.9851 | -7.4925 | -20 | 15 | -10 | -293.6664 | -258.6519 | -293.6664 | -20 | 15 | -10 | 7.4925 | 1.1333e-12 | -7.4925 | -7.4925 | 14.9851 | -7.4925 | -7.4925 | -1.3003e-12 | 7.4925 | -17.5073 | 0 | 17.5073 | -293.6664 | -258.6519 | -293.6664 | 17.5073 | 0 | -17.5073 | 64.991 | 64.991 | 64.991 | 64.5917 | 64.3386 | 64.4651 | 12 | 64.7361 | 64.7361 | 47.6445 | 47.6445 | 12 | 47.9152 | 47.9152 | 47.9152 | 47.6445 | 47.6445 | 47.6445 | 65 | 58.5015 | 61.5475 | 45 | 65 | 52.1941
ProsNet results: