## standard_case
configuration
No of prosumers |  | 3
substations |  | hydraulic: | pipe + heat exchanger |  |  | thermal: | only heat exchanger
parametrization
fluid |  | rho=1000
(water) |  | cp=4200
mu=1.0016*(10**(-3))
valve |  | K_vs=2.5 |  |  |  | 0.3584
heat exchanger |  | dotV_nom=21.504 |  | Deltap_nom=155
|  | k_nom = 5270 |  | A = 1.13
pipe1 |  | L=15 | d_hy=0.022 | epsilon=0.011 | u_nom=0.4 | zeta_instal=10 | N_layers = 2 | d_layers = [0.022, 0.024, 0.062] | lambda_layers = [395, 0.04] | h_ir=3500 | h_or=float('inf')
pipe2 |  | L=5 | d_hy=0.022 | epsilon=0.011 | u_nom=0.4 | zeta_instal=3.5 | N_layers = 2 | d_layers = [0.022, 0.024, 0.062] | lambda_layers = [395, 0.04] | h_ir=3500 | h_or=float('inf')
Scenario
T_soil |  | 12 °C
df
participation prosumers |  | pi: 1
T_in_sec | for producers | 65 °C | [5 empty] | ss
T_in_sec | for consumers | 45 °C
dotV_sec | for producers | -10 l/min
dotV_sec | for consumers | 10 l/min

## variation possibilities
configuration
topology | radial
mesh
pump model | quadratic
linear
parametrization
pump dimensioning | pump1 | type: NMT PLUS ER 25/40-180 | n_nom: 4100 | dotV_max: 55.33 l/min | Deltap_max: 402.21 hPa
| pump2 | type: NMT PLUS ER 25/60-180 | n_nom: 4100 | dotV_max: 55.17 l/min | Deltap_max: 565.06 hPa
| pump3 | type: NMT PLUS ER 25/80-180 | n_nom: 4800 | dotV_max: 57.67 l/min | Deltap_max: 751.45 hPa
scenario
mu‘s for each prosumer (mode) | producer (1) or consumer (-1)
kappa for consumers | Kappa: 0.6
Kappa. 0.9
u for producers | U: 0.6
U: 0.9

## Cases overview
Base cases
For each base case (letters), scenarios (numbers) with different control inputs are calculated. All combinations of the options for kappa and u for all prosumers are calculated. Two options for kappa (0.6 and 0.9) and two options for u (0.6 and 0.9) lead for 3 prosumers to 8 scenarios for each base case (see table on the right). 2 additional scenarios result from using different volume flow and different inlet temperatures at the secondary side.
|  |  | X-1 | X-2 | X-3 | X-4 | X-5 | X-6 | X-7 | X-8 | X-9 | X-10
|  | prosumer1 | 0.9 | 0.6 | 0.9 | 0.6 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9
|  | prosumer2 | 0.9 | 0.6 | 0.6 | 0.9 | 0.6 | 0.9 | 0.6 | 0.9 | 0.9 | 0.9
|  | prosumer3 | 0.9 | 0.6 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.6 | 0.9 | 0.9
[11 empty] | T_sec_in | dotV_sec_in
For cases with equally dimensioned pumps, pump1 is used. For cases with differently dimensioned cases pump3 is used as big pump. |  | Variations in different lengths of the pipes between two prosumers equal to a more closed valve in one prosumer. Differently dimensioned pumps are covered by the cases where pumps run on different speeds. 3 prosumers is the optimal constellation to investigate, as networks with higher amount of prosumers can be subsumed to the 3-prosumer case by grouping some prosumers.
Base case A | radial, 2 consumers, 1 producer in center, pump (quadratic)
Base case B | radial, 2 producers, 1 consumer in center, equally dimensioned pumps (quadratic)
Base case C | radial, 2 consumers, 1 producer at edge, pump (quadratic)
Base case D | radial, 2 producers, 1 consumer at edge, equally dimensioned pumps (quadratic)
Base case E | meshed, 2 consumers, 1 producer, pump (quadratic)
Base case F | meshed, 2 producers, 1 consumer, equally dimensioned pumps (quadratic)
(Base case G) | radial, 2 producers, 1 consumer in center, differently dimensioned pumps (quadratic)
(Base case H) | radial, 2 producers, 1 consumer at edge, differently dimensioned pumps (quadratic)
(Base case I) | meshed, 2 producers, 1 consumer, differently dimensioned pumps (quadratic)
((Base case J)) | radial, 2 producers, 1 consumer in center, equally dimensioned pumps (linear)
((Base case K)) | radial, 2 producers, 1 consumer in center, differently dimensioned pumps (linear)
lin
lin
lin
lin

## Case_A
Case A |  | radial, 2 consumers, 1 producer in center, pump (quadratic)
pump1 | type: NMT PLUS ER 25/40-180 |  |  | n_nom: 4100 |  | dotV_max: 55.33 l/min |  | Deltap_max: 402.21 hPa
for A-9: |  | T_1_sec_c = 40 °C |  | T_3_sec_c = 50 °C
for A-10: |  | dotV_1_sec = 15 l/min |  | dotV_2_sec = -20 l/min
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim | dotV_1 | dotV_2 | dotV_3 | dotV_1h_2h | dotV_2h_3h | dotV_1h_1c | dotV_2h_2c | dotV_3h_3c | dotV_1c_2c | dotV_2c_3c | Deltap_1h_2h | Deltap_2h_3h | Deltap_1h_1c | Deltap_2h_2c | Deltap_3h_3c | Deltap_1c_2c | Deltap_2c_3c | T_1h_2h | T_1h_1c | T_2h_1h | T_2h_3h | T_2h_2c | T_3h_2h | T_3h_3c | T_1c_1h | T_1c_2c | T_2c_2h | T_2c_1c | T_2c_3c | T_3c_3h | T_3c_2c | T_PSM1h | T_PSM1c | T_PSM2h | T_PSM2c | T_PSM3h | T_PSM3c
A-01 | -6472.5345 | 13561.1063 | -6472.5345 | -616.0372 | 55.9619 | 45.6346 | 56.2411 | 45.4223 | 55.9619 | 45.6346 | 54.2465 | 45 | 65 | 45.627 | 54.2465 | 45 | 8.9534 | -17.9068 | 8.9534 | 10 | -10 | 10 | -92.3365 | -142.336 | -92.3365 | 10 | -10 | 10 | -8.9534 | 8.9534 | 8.9534 | -17.9068 | 8.9534 | 8.9534 | -8.9534 | 24.9998 | -24.9998 | -92.3365 | -142.336 | -92.3365 | -24.9998 | 24.9998 | 55.9619 | 55.9619 | 56.2411 | 56.2411 | 56.2411 | 55.9619 | 55.9619 | 45.6346 | 45.6346 | 45.4223 | 45.4223 | 45.4223 | 45.6346 | 45.6346 | 54.2465 | 45 | 65 | 45.627 | 54.2465 | 45
A-02 | -6239.7882 | 13134.9398 | -6239.7882 | -655.3634 | 61.492 | 45.0055 | 62.0136 | 44.6613 | 61.492 | 45.0055 | 53.914 | 45 | 65 | 46.2358 | 53.914 | 45 | 5.4068 | -10.8137 | 5.4068 | 10 | -10 | 10 | -59.6592 | -77.8932 | -59.6592 | 10 | -10 | 10 | -5.4068 | 5.4068 | 5.4068 | -10.8137 | 5.4068 | 5.4068 | -5.4068 | 9.117 | -9.117 | -59.6592 | -77.8932 | -59.6592 | -9.117 | 9.117 | 61.492 | 61.492 | 62.0136 | 62.0136 | 62.0136 | 61.492 | 61.492 | 45.0055 | 45.0055 | 44.6613 | 44.6613 | 44.6613 | 45.0055 | 45.0055 | 53.914 | 45 | 65 | 46.2358 | 53.914 | 45
A-03 | -6993.5522 | 13330.7086 | -5686.5823 | -650.5741 | 60.9298 | 45.0391 | 61.3729 | 44.6964 | 60.8307 | 45.0024 | 54.9908 | 45 | 65 | 45.9561 | 53.1237 | 45 | 6.2872 | -11.4196 | 5.1324 | 10 | -10 | 10 | -45.5313 | -70.1862 | -53.7564 | 10 | -10 | 10 | -6.2872 | 5.1324 | 6.2872 | -11.4196 | 5.1324 | 6.2872 | -5.1324 | 12.3274 | -8.2149 | -45.5313 | -70.1862 | -53.7564 | -12.3274 | 8.2149 | 60.9298 | 60.9298 | 61.3729 | 61.3729 | 61.3729 | 60.8307 | 60.8307 | 45.0391 | 45.0391 | 44.6964 | 44.7425 | 44.6399 | 45.0024 | 45.0024 | 54.9908 | 45 | 65 | 45.9561 | 53.1237 | 45
A-04 | -6544.2713 | 13709.6155 | -6544.2713 | -621.0729 | 56.8753 | 45.348 | 57.1901 | 45.1158 | 56.8753 | 45.348 | 54.349 | 45 | 65 | 45.4148 | 54.349 | 45 | 8.1103 | -16.2205 | 8.1103 | 10 | -10 | 10 | -134.2333 | -175.2597 | -134.2333 | 10 | -10 | 10 | -8.1103 | 8.1103 | 8.1103 | -16.2205 | 8.1103 | 8.1103 | -8.1103 | 20.5132 | -20.5132 | -134.2333 | -175.2597 | -134.2333 | -20.5132 | 20.5132 | 56.8753 | 56.8753 | 57.1901 | 57.1901 | 57.1901 | 56.8753 | 56.8753 | 45.348 | 45.348 | 45.1158 | 45.1158 | 45.1158 | 45.348 | 45.348 | 54.349 | 45 | 65 | 45.4148 | 54.349 | 45
A-05 | -5686.5823 | 13330.7086 | -6993.5522 | -650.5741 | 60.8307 | 45.0024 | 61.3729 | 44.6964 | 60.9298 | 45.0391 | 53.1237 | 45 | 65 | 45.9561 | 54.9908 | 45 | 5.1324 | -11.4196 | 6.2872 | 10 | -10 | 10 | -53.7564 | -70.1862 | -45.5313 | 10 | -10 | 10 | -5.1324 | 6.2872 | 5.1324 | -11.4196 | 6.2872 | 5.1324 | -6.2872 | 8.2149 | -12.3274 | -53.7564 | -70.1862 | -45.5313 | -8.2149 | 12.3274 | 60.8307 | 60.8307 | 61.3729 | 61.3729 | 61.3729 | 60.9298 | 60.9298 | 45.0024 | 45.0024 | 44.6964 | 44.6399 | 44.7425 | 45.0391 | 45.0391 | 53.1237 | 45 | 65 | 45.9561 | 54.9908 | 45
A-06 | -6004.4446 | 13573.2978 | -6950.0078 | -618.8454 | 56.3608 | 45.2188 | 56.6886 | 45.3686 | 56.4208 | 45.893 | 53.5778 | 45 | 65 | 45.6096 | 54.9286 | 45 | 7.6986 | -17.1294 | 9.4308 | 10 | -10 | 10 | -120.9519 | -157.919 | -102.4455 | 10 | -10 | 10 | -7.6986 | 9.4308 | 7.6986 | -17.1294 | 9.4308 | 7.6986 | -9.4308 | 18.4836 | -27.7368 | -120.9519 | -157.919 | -102.4455 | -18.4836 | 27.7368 | 56.3608 | 56.3608 | 56.6886 | 56.6886 | 56.6886 | 56.4208 | 56.4208 | 45.2188 | 45.2188 | 45.3686 | 44.9751 | 45.6899 | 45.893 | 45.893 | 53.5778 | 45 | 65 | 45.6096 | 54.9286 | 45
A-07 | -6412.0282 | 13470.4891 | -6412.0282 | -646.4326 | 60.3661 | 45.0198 | 60.8276 | 44.7078 | 60.3661 | 45.0198 | 54.16 | 45 | 65 | 45.7564 | 54.16 | 45 | 5.9689 | -11.9378 | 5.9689 | 10 | -10 | 10 | -41.0384 | -63.2604 | -41.0384 | 10 | -10 | 10 | -5.9689 | 5.9689 | 5.9689 | -11.9378 | 5.9689 | 5.9689 | -5.9689 | 11.111 | -11.111 | -41.0384 | -63.2604 | -41.0384 | -11.111 | 11.111 | 60.3661 | 60.3661 | 60.8276 | 60.8276 | 60.8276 | 60.3661 | 60.3661 | 45.0198 | 45.0198 | 44.7078 | 44.7078 | 44.7078 | 45.0198 | 45.0198 | 54.16 | 45 | 65 | 45.7564 | 54.16 | 45
A-08 | -6950.0078 | 13573.2978 | -6004.4446 | -618.8454 | 56.4208 | 45.893 | 56.6886 | 45.3686 | 56.3608 | 45.2188 | 54.9286 | 45 | 65 | 45.6096 | 53.5778 | 45 | 9.4308 | -17.1294 | 7.6986 | 10 | -10 | 10 | -102.4455 | -157.919 | -120.9519 | 10 | -10 | 10 | -9.4308 | 7.6986 | 9.4308 | -17.1294 | 7.6986 | 9.4308 | -7.6986 | 27.7368 | -18.4836 | -102.4455 | -157.919 | -120.9519 | -27.7368 | 18.4836 | 56.4208 | 56.4208 | 56.6886 | 56.6886 | 56.6886 | 56.3608 | 56.3608 | 45.893 | 45.893 | 45.3686 | 45.6899 | 44.9751 | 45.2188 | 45.2188 | 54.9286 | 45 | 65 | 45.6096 | 53.5778 | 45
A-09 | -9424.8103 | 13561.1063 | -3520.2588 | -616.0372 | 55.9619 | 40.924 | 56.2411 | 45.4223 | 55.9619 | 50.3451 | 53.464 | 40 | 65 | 45.627 | 55.0289 | 50 | 8.9534 | -17.9068 | 8.9534 | 10 | -10 | 10 | -92.3365 | -142.336 | -92.3365 | 10 | -10 | 10 | -8.9534 | 8.9534 | 8.9534 | -17.9068 | 8.9534 | 8.9534 | -8.9534 | 24.9998 | -24.9998 | -92.3365 | -142.336 | -92.3365 | -24.9998 | 24.9998 | 55.9619 | 55.9619 | 56.2411 | 56.2411 | 56.2411 | 55.9619 | 55.9619 | 40.924 | 40.924 | 45.4223 | 40.7415 | 50.1031 | 50.3451 | 50.3451 | 53.464 | 40 | 65 | 45.627 | 55.0289 | 50
A-10 | -10520.8968 | 21184.4438 | -10000.4925 | -663.0545 | 61.9369 | 45.1501 | 62.2541 | 45.3535 | 61.9369 | 45.9805 | 55.0199 | 45 | 65 | 49.8683 | 59.2864 | 45 | 8.9534 | -17.9068 | 8.9534 | 15 | -20 | 10 | -92.3365 | -142.336 | -92.3365 | 15 | -20 | 10 | -8.9534 | 8.9534 | 8.9534 | -17.9068 | 8.9534 | 8.9534 | -8.9534 | 24.9998 | -24.9998 | -92.3365 | -142.336 | -92.3365 | -24.9998 | 24.9998 | 61.9369 | 61.9369 | 62.2541 | 62.2541 | 62.2541 | 61.9369 | 61.9369 | 45.1501 | 45.1501 | 45.3535 | 44.9409 | 45.766 | 45.9805 | 45.9805 | 55.0199 | 45 | 65 | 49.8683 | 59.2864 | 45
ProsNet results:
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim
A-1 | -6097.56 | 12814.88 | -6097.56 | -619.76 | 56.05 | 46.26 | 56.33 | 46.04 | 56.05 | 46.26 | 53.74 | 45 | 65 | 46.62 | 53.74 | 45 | 8.93 | -17.86 | 8.93 | 10 | -10 | 10 | -91.57 | -141.44 | -91.57
A-2 | -5752.83 | 12152.18 | -5752.83 | -646.52 | 60.63 | 45.18 | 61.15 | 44.83 | 60.63 | 45.18 | 53.25 | 45 | 65 | 47.57 | 53.25 | 45 | 5.34 | -10.68 | 5.34 | 10 | -10 | 10 | -58.49 | -78.11 | -58.49
A-3 | -6414.41 | 12340.68 | -5282.9 | -643.38 | 60.19 | 45.39 | 60.63 | 44.94 | 60.09 | 45.13 | 54.2 | 45 | 65 | 47.3 | 52.58 | 45 | 6.21 | -11.27 | 5.06 | 10 | -10 | 10 | -44.67 | -70.48 | -52.65
A-4 | -6134 | 12891.37 | -6134 | -623.38 | 56.83 | 45.95 | 57.15 | 45.71 | 56.83 | 45.95 | 53.8 | 45 | 65 | 46.51 | 53.8 | 45 | 8.08 | -16.16 | 8.08 | 10 | -10 | 10 | -133.02 | -174.6 | -133.02
A-5 | -5282.9 | 12340.68 | -6414.41 | -643.38 | 60.09 | 45.13 | 60.63 | 44.94 | 60.19 | 45.39 | 52.58 | 45 | 65 | 47.3 | 54.2 | 45 | 5.06 | -11.27 | 6.21 | 10 | -10 | 10 | -52.65 | -70.48 | -44.67
A-6 | -5680.87 | 12811.03 | -6508.49 | -621.68 | 56.38 | 45.74 | 56.71 | 45.96 | 56.45 | 46.55 | 53.15 | 45 | 65 | 46.63 | 54.33 | 45 | 7.65 | -17.08 | 9.43 | 10 | -10 | 10 | -119.4 | -157.06 | -101.98
A-7 | -5933.79 | 12508.05 | -5933.79 | -640.46 | 59.73 | 45.29 | 60.19 | 44.97 | 59.73 | 45.29 | 53.51 | 45 | 65 | 47.06 | 53.51 | 45 | 5.89 | -11.78 | 5.89 | 10 | -10 | 10 | -40.22 | -63.67 | -40.22
A-8 | -6508.49 | 12811.03 | -5680.87 | -621.68 | 56.45 | 46.55 | 56.71 | 45.96 | 56.38 | 45.74 | 54.33 | 45 | 65 | 46.63 | 53.15 | 45 | 9.43 | -17.08 | 7.65 | 10 | -10 | 10 | -101.98 | -157.06 | -119.4
A-9 | -8856.46 | 12814.88 | -3338.65 | -619.76 | 56.05 | 41.83 | 56.33 | 46.04 | 56.05 | 50.69 | 52.7 | 40 | 65 | 46.62 | 54.79 | 50 | 8.93 | -17.86 | 8.93 | 10 | -10 | 10 | -91.57 | -141.44 | -91.57
A-10 | -10079.7 | 19980.39 | -9236.02 | -664.68 | 61.74 | 45.55 | 62.06 | 46.01 | 61.74 | 46.9 | 54.64 | 45 | 65 | 50.67 | 58.24 | 45 | 8.93 | -17.86 | 8.93 | 15 | -20 | 10 | -91.57 | -141.44 | -91.57
| Err dotQ_1 | Err dotQ_2 | Err dotQ_3 | Err sum_dotQ_loss | Err T_1_prim_hot | Err T_1_prim_cold | Err T_2_prim_hot | Err T_2_prim_cold | Err T_3_prim_hot | Err T_3_prim_cold | Err T_1_sec_hot | Err T_1_sec_cold | Err T_2_sec_hot | Err T_2_sec_cold | Err T_3_sec_hot | Err T_3_sec_cold | Err dotV_1_prim | Err dotV_2_prim | Err dotV_3_prim | Err dotV_1_sec | Err dotV_2_sec | Err dotV_3_sec | Err Deltap_1_prim | Err Deltap_2_prim | Err Deltap_3_prim
A-01 | 6.1496 | 5.8231 | 6.1496 | -0.60069 | -0.088059 | -0.62542 | -0.088859 | -0.61768 | -0.088059 | -0.62542 | 0.50648 | 0 | 0 | -0.99301 | 0.50648 | 0 | 0.26182 | 0.26182 | 0.26182 | 0 | 0 | 0 | 0.83703 | 0.63349 | 0.83703
A-02 | 8.4647 | 8.0871 | 8.4647 | 1.3678 | 0.86197 | -0.17449 | 0.86355 | -0.1687 | 0.86197 | -0.17449 | 0.66398 | 0 | 0 | -1.3342 | 0.66398 | 0 | 1.2519 | 1.2519 | 1.2519 | 0 | 0 | 0 | 1.9991 | -0.27758 | 1.9991
A-03 | 9.0288 | 8.0225 | 7.6413 | 1.1182 | 0.73981 | -0.35093 | 0.74294 | -0.24357 | 0.74066 | -0.12759 | 0.79079 | 0 | 0 | -1.3439 | 0.54369 | 0 | 1.2428 | 1.3272 | 1.4308 | 0 | 0 | 0 | 1.9282 | -0.4168 | 2.1015
A-04 | 6.6885 | 6.3472 | 6.6885 | -0.3701 | 0.045342 | -0.60196 | 0.040075 | -0.59422 | 0.045342 | -0.60196 | 0.54896 | 0 | 0 | -1.0952 | 0.54896 | 0 | 0.37467 | 0.37467 | 0.37467 | 0 | 0 | 0 | 0.91212 | 0.37781 | 0.91212
A-05 | 7.6413 | 8.0225 | 9.0288 | 1.1182 | 0.74066 | -0.12759 | 0.74294 | -0.24357 | 0.73981 | -0.35093 | 0.54369 | 0 | 0 | -1.3439 | 0.79079 | 0 | 1.4308 | 1.3272 | 1.2428 | 0 | 0 | 0 | 2.1015 | -0.4168 | 1.9282
A-06 | 5.6959 | 5.9501 | 6.7837 | -0.45597 | -0.019206 | -0.5212 | -0.021384 | -0.59138 | -0.029175 | -0.65704 | 0.42778 | 0 | 0 | -1.0204 | 0.59858 | 0 | 0.6353 | 0.28902 | 0.0081078 | 0 | 0 | 0 | 1.2998 | 0.54695 | 0.45648
A-07 | 8.0596 | 7.6946 | 8.0596 | 0.93256 | 0.63607 | -0.27016 | 0.63756 | -0.26224 | 0.63607 | -0.27016 | 0.65004 | 0 | 0 | -1.3036 | 0.65004 | 0 | 1.3399 | 1.3399 | 1.3399 | 0 | 0 | 0 | 2.0349 | -0.64324 | 2.0349
A-08 | 6.7837 | 5.9501 | 5.6959 | -0.45597 | -0.029175 | -0.65704 | -0.021384 | -0.59138 | -0.019206 | -0.5212 | 0.59858 | 0 | 0 | -1.0204 | 0.42778 | 0 | 0.0081079 | 0.28902 | 0.6353 | 0 | 0 | 0 | 0.45648 | 0.54695 | 1.2998
A-09 | 6.4174 | 5.8231 | 5.4396 | -0.60069 | -0.088059 | -0.90597 | -0.088859 | -0.61768 | -0.088059 | -0.34487 | 0.76401 | 0 | 0 | -0.99301 | 0.23894 | 0 | 0.26182 | 0.26182 | 0.26182 | 0 | 0 | 0 | 0.83703 | 0.63349 | 0.83703
A-10 | 4.3771 | 6.0262 | 8.2771 | -0.24455 | 0.19692 | -0.39987 | 0.19407 | -0.65653 | 0.19692 | -0.91953 | 0.3799 | 0 | 0 | -0.80175 | 1.0464 | 0 | 0.26182 | 0.26182 | 0.26182 | 0 | 0 | 0 | 0.83703 | 0.63349 | 0.83703

## Case_B
Case B |  | radial, 2 producers, 1 consumer in center, equally dimensioned pumps (quadratic)
pump1 | type: NMT PLUS ER 25/40-180 |  |  | n_nom: 4100 |  | dotV_max: 55.33 l/min |  | Deltap_max: 402.21 hPa
for B-9: |  | T_1_sec_h = 50 °C |  | T_2_sec_c = 40 °C
for B-10: |  | dotV_1_sec = -20 l/min |  | dotV_2_sec = 15 l/min
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim | dotV_1 | dotV_2 | dotV_3 | dotV_1h_2h | dotV_2h_3h | dotV_1h_1c | dotV_2h_2c | dotV_3h_3c | dotV_1c_2c | dotV_2c_3c | Deltap_1h_2h | Deltap_2h_3h | Deltap_1h_1c | Deltap_2h_2c | Deltap_3h_3c | Deltap_1c_2c | Deltap_2c_3c | T_1h_2h | T_1h_1c | T_2h_1h | T_2h_3h | T_2h_2c | T_3h_2h | T_3h_3c | T_1c_1h | T_1c_2c | T_2c_2h | T_2c_1c | T_2c_3c | T_3c_3h | T_3c_2c | T_PSM1h | T_PSM1c | T_PSM2h | T_PSM2c | T_PSM3h | T_PSM3c
B-01 | 7015.4034 | -13299.4536 | 7015.4034 | -731.3532 | 64.7934 | 51.4175 | 64.3955 | 51.7169 | 64.7934 | 51.4175 | 65 | 54.978 | 63.9992 | 45 | 65 | 54.978 | -7.4926 | 14.9852 | -7.4926 | -10 | 10 | -10 | -293.6715 | -258.6563 | -293.6715 | -10 | 10 | -10 | 7.4926 | -7.4926 | -7.4926 | 14.9852 | -7.4926 | -7.4926 | 7.4926 | -17.5076 | 17.5076 | -293.6715 | -258.6563 | -293.6715 | 17.5076 | -17.5076 | 64.7934 | 64.7934 | 64.3955 | 64.3955 | 64.3955 | 64.7934 | 64.7934 | 51.4175 | 51.4175 | 51.7169 | 51.7169 | 51.7169 | 51.4175 | 51.4175 | 65 | 54.978 | 63.9992 | 45 | 65 | 54.978
B-02 | 5516.3874 | -10351.7148 | 5516.3872 | -681.0598 | 65 | 44.9649 | 64.2417 | 45.4434 | 65 | 44.9649 | 65 | 57.1194 | 59.7882 | 45 | 65 | 57.1194 | -3.9334 | 7.8668 | -3.9334 | -10 | 10 | -10 | -135.9439 | -126.2939 | -135.9439 | -10 | 10 | -10 | 3.9334 | -3.9334 | -3.9334 | 7.8668 | -3.9334 | -3.9334 | 3.9334 | -4.825 | 4.825 | -135.9439 | -126.2939 | -135.9439 | 4.825 | -4.825 | 65 | 65 | 64.2417 | 64.2417 | 64.2417 | 65 | 65 | 44.9649 | 44.9649 | 45.4434 | 45.4434 | 45.4434 | 44.9649 | 44.9649 | 65 | 57.1194 | 59.7882 | 45 | 65 | 57.1194
B-04 | 6417.8278 | -12151.7245 | 6417.8278 | -694.6754 | 64.9982 | 46.6434 | 64.4002 | 47.0388 | 64.9982 | 46.6434 | 65 | 55.8317 | 62.3596 | 45 | 65 | 55.8317 | -4.9951 | 9.9901 | -4.9951 | -10 | 10 | -10 | -130.5206 | -114.9584 | -130.5206 | -10 | 10 | -10 | 4.9951 | -4.9951 | -4.9951 | 9.9901 | -4.9951 | -4.9951 | 4.9951 | -7.7811 | 7.7811 | -130.5206 | -114.9584 | -130.5206 | 7.7811 | -7.7811 | 64.9982 | 64.9982 | 64.4002 | 64.4002 | 64.4002 | 64.9982 | 64.9982 | 46.6434 | 46.6434 | 47.0388 | 47.0388 | 47.0388 | 46.6434 | 46.6434 | 65 | 55.8317 | 62.3596 | 45 | 65 | 55.8317
B-07 | 6801.5291 | -12893.4804 | 6801.5291 | -709.5779 | 64.9817 | 48.5133 | 64.4751 | 48.8658 | 64.9817 | 48.5133 | 65 | 55.2835 | 63.4193 | 45 | 65 | 55.2835 | -5.9001 | 11.8002 | -5.9001 | -10 | 10 | -10 | -305.8738 | -284.1614 | -305.8738 | -10 | 10 | -10 | 5.9001 | -5.9001 | -5.9001 | 11.8002 | -5.9001 | -5.9001 | 5.9001 | -10.8562 | 10.8562 | -305.8738 | -284.1614 | -305.8738 | 10.8562 | -10.8562 | 64.9817 | 64.9817 | 64.4751 | 64.4751 | 64.4751 | 64.9817 | 64.9817 | 48.5133 | 48.5133 | 48.8658 | 48.8658 | 48.8658 | 48.5133 | 48.5133 | 65 | 55.2835 | 63.4193 | 45 | 65 | 55.2835
B-09 | 2260.0937 | -11641.6359 | 10007.6609 | -626.1187 | 49.9334 | 45.6243 | 56.9778 | 45.8796 | 64.7053 | 45.6243 | 50 | 46.7713 | 56.6309 | 40 | 65 | 50.7033 | -7.4926 | 14.9852 | -7.4926 | -10 | 10 | -10 | -293.6715 | -258.6563 | -293.6715 | -10 | 10 | -10 | 7.4926 | -7.4926 | -7.4926 | 14.9852 | -7.4926 | -7.4926 | 7.4926 | -17.5076 | 17.5076 | -293.6715 | -258.6563 | -293.6715 | 17.5076 | -17.5076 | 49.9334 | 49.9334 | 49.6476 | 64.3081 | 56.9778 | 64.7053 | 64.7053 | 45.6243 | 45.6243 | 45.8796 | 45.8796 | 45.8796 | 45.6243 | 45.6243 | 50 | 46.7713 | 56.6309 | 40 | 65 | 50.7033
B-10 | 9097.9326 | -17374.8617 | 8964.1865 | -701.8529 | 64.991 | 47.6445 | 64.4651 | 47.9152 | 64.736 | 47.6445 | 65 | 58.5015 | 61.5475 | 45 | 65 | 52.194 | -7.4926 | 14.9852 | -7.4926 | -20 | 15 | -10 | -293.6715 | -258.6563 | -293.6715 | -20 | 15 | -10 | 7.4926 | -7.4926 | -7.4926 | 14.9852 | -7.4926 | -7.4926 | 7.4926 | -17.5076 | 17.5076 | -293.6715 | -258.6563 | -293.6715 | 17.5076 | -17.5076 | 64.991 | 64.991 | 64.5917 | 64.3386 | 64.4651 | 64.736 | 64.736 | 47.6445 | 47.6445 | 47.9152 | 47.9152 | 47.9152 | 47.6445 | 47.6445 | 65 | 58.5015 | 61.5475 | 45 | 65 | 52.194
ProsNet results:
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim
B-1 | 6577.35 | -12429.32 | 6577.35 | -725.38 | 64.21 | 51.58 | 63.82 | 51.88 | 64.21 | 51.58 | 65 | 55.57 | 62.82 | 45 | 65 | 55.57 | -7.47 | 14.94 | -7.47 | -10 | 10 | -10 | -289.77 | -253.75 | -289.77
B-2 | 5184.07 | -9685.34 | 5184.07 | -682.78 | 64.97 | 45.83 | 64.2 | 46.32 | 64.97 | 45.83 | 65 | 57.57 | 58.89 | 45 | 65 | 57.57 | -3.88 | 7.77 | -3.88 | -10 | 10 | -10 | -133.95 | -122.96 | -133.95
B-3 | 10420.53 | -10001.66 | 93.96 | -509.79 | 62.22 | 47.35 | 61.94 | 47.61 | 31.82 | 64.98 | 65 | 50.06 | 59.34 | 45 | 65 | 64.87 | -10.05 | 10.01 | 0.04 | -10 | 10 | -10 | -265.01 | -203.13 | -203.09
B-4 | 5971.21 | -11245.63 | 5971.21 | -696.78 | 64.87 | 47.53 | 64.27 | 47.94 | 64.87 | 47.53 | 65 | 56.44 | 61.13 | 45 | 65 | 56.44 | -4.94 | 9.87 | -4.94 | -10 | 10 | -10 | -128.77 | -111.73 | -128.77
B-5 | 93.57 | -10001.64 | 10420.68 | -509.74 | 32.12 | 64.98 | 61.94 | 47.61 | 62.22 | 47.35 | 65 | 64.87 | 59.34 | 45 | 65 | 50.06 | 0.04 | 10.01 | -10.05 | -10 | 10 | -10 | -203.09 | -203.13 | -265.01
B-6 | 3.33 | -9868.75 | 10257.12 | -389.04 | 20.75 | 23.73 | 60.79 | 48.82 | 61.02 | 48.6 | 65 | 65 | 59.15 | 45 | 65 | 50.29 | 0.02 | 11.83 | -11.84 | -10 | 10 | -10 | -159.73 | -159.74 | -243.36
B-7 | 6338.41 | -11967.32 | 6338.41 | -709.48 | 64.7 | 49.2 | 64.19 | 49.56 | 64.7 | 49.2 | 65 | 55.91 | 62.16 | 45 | 65 | 55.91 | -5.87 | 11.73 | -5.87 | -10 | 10 | -10 | -301.66 | -278.4 | -301.66
B-8 | 10256.29 | -9868.95 | 3.52 | -380.86 | 61.02 | 48.6 | 60.79 | 48.82 | 18.4 | 21.55 | 65 | 50.29 | 59.15 | 45 | 65 | 64.99 | -11.84 | 11.83 | 0.02 | -10 | 10 | -10 | -243.36 | -159.74 | -159.73
B-9 | 2074.41 | -10880.38 | 9426.91 | -620.94 | 49.75 | 45.77 | 56.47 | 46.03 | 63.87 | 45.77 | 50 | 47.03 | 55.6 | 40 | 65 | 51.48 | -7.47 | 14.94 | -7.47 | -10 | 10 | -10 | -289.77 | -253.75 | -289.77
B-10 | 8760.31 | -16350.95 | 8290.22 | -699.57 | 64.91 | 48.09 | 64.06 | 48.36 | 64 | 48.09 | 65 | 58.72 | 60.63 | 45 | 65 | 53.11 | -7.47 | 14.94 | -7.47 | -20 | 15 | -10 | -289.77 | -253.75 | -289.77
| Err dotQ_1 | Err dotQ_2 | Err dotQ_3 | Err sum_dotQ_loss | Err T_1_prim_hot | Err T_1_prim_cold | Err T_2_prim_hot | Err T_2_prim_cold | Err T_3_prim_hot | Err T_3_prim_cold | Err T_1_sec_hot | Err T_1_sec_cold | Err T_2_sec_hot | Err T_2_sec_cold | Err T_3_sec_hot | Err T_3_sec_cold | Err dotV_1_prim | Err dotV_2_prim | Err dotV_3_prim | Err dotV_1_sec | Err dotV_2_sec | Err dotV_3_sec | Err Deltap_1_prim | Err Deltap_2_prim | Err Deltap_3_prim
B-01 | 6.66 | 7.0007 | 6.66 | 0.82346 | 0.58342 | -0.16246 | 0.57554 | -0.16313 | 0.58342 | -0.16246 | 0 | -0.592 | 1.1792 | 0 | 0 | -0.592 | 0.30241 | 0.30241 | 0.30241 | 0 | 0 | 0 | 1.3464 | 1.9335 | 1.3464
B-02 | 6.4104 | 6.8802 | 6.4104 | -0.25194 | 0.029976 | -0.86506 | 0.041687 | -0.87657 | 0.029976 | -0.86506 | 0 | -0.45055 | 0.89816 | 0 | 0 | -0.45055 | 1.3759 | 1.2455 | 1.3759 | 0 | 0 | 0 | 1.4885 | 2.7114 | 1.4885
B-04 | 7.4795 | 8.0573 | 7.4795 | -0.30205 | 0.12818 | -0.88661 | 0.13016 | -0.90125 | 0.12818 | -0.88661 | 0 | -0.60833 | 1.2296 | 0 | 0 | -0.60833 | 1.1146 | 1.217 | 1.1146 | 0 | 0 | 0 | 1.3595 | 2.8894 | 1.3595
B-07 | 7.3066 | 7.7391 | 7.3066 | 0.0138 | 0.28167 | -0.6867 | 0.2851 | -0.69422 | 0.28167 | -0.6867 | 0 | -0.62647 | 1.2593 | 0 | 0 | -0.62647 | 0.51244 | 0.59812 | 0.51244 | 0 | 0 | 0 | 1.3969 | 2.0695 | 1.3969
B-09 | 8.9512 | 6.9966 | 6.1606 | 0.83401 | 0.18345 | -0.14575 | 0.50783 | -0.15041 | 0.83531 | -0.14575 | 0 | -0.25871 | 1.0309 | 0 | 0 | -0.77666 | 0.30241 | 0.30241 | 0.30241 | 0 | 0 | 0 | 1.3464 | 1.9335 | 1.3464
B-10 | 3.854 | 6.2621 | 8.1297 | 0.32633 | 0.081047 | -0.44549 | 0.40513 | -0.44481 | 0.73604 | -0.44549 | 0 | -0.21852 | 0.91749 | 0 | 0 | -0.91598 | 0.30241 | 0.30241 | 0.30241 | 0 | 0 | 0 | 1.3464 | 1.9335 | 1.3464

## Case_C
Case C |  | radial, 2 consumers, 1 producer at edge, pump (quadratic)
pump1 | type: NMT PLUS ER 25/40-180 |  |  | n_nom: 4100 |  | dotV_max: 55.33 l/min |  | Deltap_max: 402.21 hPa
for C-9: |  | T_1_sec_h = 50 °C |  | T_2_sec_c = 40 °C
for C-10: |  | dotV_1_sec = -20 l/min |  | dotV_2_sec = 15 l/min
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim | dotV_1 | dotV_2 | dotV_3 | dotV_1h_2h | dotV_2h_3h | dotV_1h_1c | dotV_2h_2c | dotV_3h_3c | dotV_1c_2c | dotV_2c_3c | Deltap_1h_2h | Deltap_2h_3h | Deltap_1h_1c | Deltap_2h_2c | Deltap_3h_3c | Deltap_1c_2c | Deltap_2c_3c | T_1h_2h | T_1h_1c | T_2h_1h | T_2h_3h | T_2h_2c | T_3h_2h | T_3h_3c | T_1c_1h | T_1c_2c | T_2c_2h | T_2c_1c | T_2c_3c | T_3c_3h | T_3c_2c | T_PSM1h | T_PSM1c | T_PSM2h | T_PSM2c | T_PSM3h | T_PSM3c
C-01 | 13700.1023 | -7261.9535 | -5809.7752 | -628.3736 | 58.4582 | 44.962 | 58.277 | 45.3611 | 57.8733 | 45.044 | 65 | 45.4284 | 55.3742 | 45 | 53.2997 | 45 | -14.5014 | 8.0321 | 6.4693 | -10 | 10 | 10 | -205.4761 | -74.3121 | -48.2079 | -10 | 10 | 10 | 14.5014 | 6.4693 | -14.5014 | 8.0321 | 6.4693 | -14.5014 | -6.4693 | -65.582 | -13.0521 | -205.4761 | -74.3121 | -48.2079 | 65.582 | 13.0521 | 58.4582 | 58.4582 | 58.277 | 58.277 | 58.277 | 57.8733 | 57.8733 | 44.962 | 44.962 | 45.3611 | 45.0911 | 44.7558 | 45.044 | 45.044 | 65 | 45.4284 | 55.3742 | 45 | 53.2997 | 45
C-02 | 12113.8143 | -6212.2862 | -5234.3285 | -667.1997 | 63.7566 | 44.5895 | 63.4327 | 45.001 | 62.7454 | 45.0001 | 65 | 47.6946 | 53.8747 | 45 | 52.4776 | 45 | -9.0288 | 4.8149 | 4.2138 | -10 | 10 | 10 | -98.1566 | -47.3116 | -36.2364 | -10 | 10 | 10 | 9.0288 | 4.2138 | -9.0288 | 4.8149 | 4.2138 | -9.0288 | -4.2138 | -25.4225 | -5.5376 | -98.1566 | -47.3116 | -36.2364 | 25.4225 | 5.5376 | 63.7566 | 63.7566 | 63.4327 | 63.4327 | 63.4327 | 62.7454 | 62.7454 | 44.5895 | 44.5895 | 45.001 | 44.7948 | 44.5592 | 45.0001 | 45.0001 | 65 | 47.6946 | 53.8747 | 45 | 52.4776 | 45
C-03 | 13690.5364 | -7034.4471 | -6022.0347 | -634.0546 | 59.2638 | 44.8226 | 59.0664 | 45.1524 | 58.6462 | 45.0357 | 65 | 45.4421 | 55.0492 | 45 | 53.6029 | 45 | -13.5431 | 7.2224 | 6.3208 | -10 | 10 | 10 | -220.8523 | -106.451 | -81.532 | -10 | 10 | 10 | 13.5431 | 6.3208 | -13.5431 | 7.2224 | 6.3208 | -13.5431 | -6.3208 | -57.2006 | -12.4595 | -220.8523 | -106.451 | -81.532 | 57.2006 | 12.4595 | 59.2638 | 59.2638 | 59.0664 | 59.0664 | 59.0664 | 58.6462 | 58.6462 | 44.8226 | 44.8226 | 45.1524 | 44.9603 | 44.7407 | 45.0357 | 45.0357 | 65 | 45.4421 | 55.0492 | 45 | 53.6029 | 45
C-04 | 12430.9405 | -7218.4284 | -4548.4399 | -664.0722 | 63.3716 | 44.616 | 63.0649 | 45.0131 | 62.3001 | 45 | 65 | 47.2415 | 55.312 | 45 | 51.4978 | 45 | -9.4684 | 5.7124 | 3.7559 | -10 | 10 | 10 | -93.5043 | -37.5875 | -28.7887 | -10 | 10 | 10 | 9.4684 | 3.7559 | -9.4684 | 5.7124 | 3.7559 | -9.4684 | -3.7559 | -27.9584 | -4.3994 | -93.5043 | -37.5875 | -28.7887 | 27.9584 | 4.3994 | 63.3716 | 63.3716 | 63.0649 | 63.0649 | 63.0649 | 62.3001 | 62.3001 | 44.616 | 44.616 | 45.0131 | 44.8118 | 44.5057 | 45 | 45 | 65 | 47.2415 | 55.312 | 45 | 51.4978 | 45
C-05 | 12324.2469 | -5724.1049 | -5934.459 | -665.683 | 63.5162 | 44.6017 | 63.2034 | 45.0003 | 62.6043 | 45.001 | 65 | 47.3939 | 53.1773 | 45 | 53.4778 | 45 | -9.3083 | 4.4922 | 4.816 | -10 | 10 | 10 | -95.2244 | -41.1828 | -26.7162 | -10 | 10 | 10 | 9.3083 | 4.816 | -9.3083 | 4.4922 | 4.816 | -9.3083 | -4.816 | -27.0208 | -7.2333 | -95.2244 | -41.1828 | -26.7162 | 27.0208 | 7.2333 | 63.5162 | 63.5162 | 63.2034 | 63.2034 | 63.2034 | 62.6043 | 62.6043 | 44.6017 | 44.6017 | 45.0003 | 44.8009 | 44.6148 | 45.001 | 45.001 | 65 | 47.3939 | 53.1773 | 45 | 53.4778 | 45
C-06 | 12563.5025 | -6701.7726 | -5198.7729 | -662.957 | 63.1838 | 44.6189 | 62.8846 | 45.0052 | 62.2202 | 45.0001 | 65 | 47.0521 | 54.574 | 45 | 52.4268 | 45 | -9.6676 | 5.3547 | 4.3129 | -10 | 10 | 10 | -91.3227 | -33.0276 | -21.4257 | -10 | 10 | 10 | 9.6676 | 4.3129 | -9.6676 | 5.3547 | 4.3129 | -9.6676 | -4.3129 | -29.1476 | -5.8009 | -91.3227 | -33.0276 | -21.4257 | 29.1476 | 5.8009 | 63.1838 | 63.1838 | 62.8846 | 62.8846 | 62.8846 | 62.2202 | 62.2202 | 44.6189 | 44.6189 | 45.0052 | 44.8107 | 44.5693 | 45.0001 | 45.0001 | 65 | 47.0521 | 54.574 | 45 | 52.4268 | 45
C-07 | 13727.4471 | -6426.5259 | -6669.1175 | -631.8036 | 58.8881 | 44.8428 | 58.6981 | 45.0735 | 58.3332 | 45.1448 | 65 | 45.3894 | 54.1808 | 45 | 54.5273 | 45 | -13.9624 | 6.7384 | 7.224 | -10 | 10 | 10 | -214.2548 | -92.6612 | -60.1114 | -10 | 10 | 10 | 13.9624 | 7.224 | -13.9624 | 6.7384 | 7.224 | -13.9624 | -7.224 | -60.7968 | -16.2749 | -214.2548 | -92.6612 | -60.1114 | 60.7968 | 16.2749 | 58.8881 | 58.8881 | 58.6981 | 58.6981 | 58.6981 | 58.3332 | 58.3332 | 44.8428 | 44.8428 | 45.0735 | 44.9764 | 44.8857 | 45.1448 | 45.1448 | 65 | 45.3894 | 54.1808 | 45 | 54.5273 | 45
C-08 | 13579.8715 | -7784.4644 | -5164.5137 | -630.8933 | 58.7558 | 45.0964 | 58.5696 | 45.5913 | 58.1034 | 45.0078 | 65 | 45.6002 | 56.1207 | 45 | 52.3779 | 45 | -14.2026 | 8.5687 | 5.6339 | -10 | 10 | 10 | -210.3847 | -84.5719 | -64.7746 | -10 | 10 | 10 | 14.2026 | 5.6339 | -14.2026 | 8.5687 | 5.6339 | -14.2026 | -5.6339 | -62.9064 | -9.8987 | -210.3847 | -84.5719 | -64.7746 | 62.9064 | 9.8987 | 58.7558 | 58.7558 | 58.5696 | 58.5696 | 58.5696 | 58.1034 | 58.1034 | 45.0964 | 45.0964 | 45.5913 | 45.2288 | 44.6774 | 45.0078 | 45.0078 | 65 | 45.6002 | 56.1207 | 45 | 52.3779 | 45
C-09 | 5403.3457 | -3982.8007 | -890.8574 | -529.6877 | 47.4199 | 42.097 | 47.2817 | 40.198 | 46.974 | 45.0068 | 50 | 42.2809 | 45.6897 | 40 | 46.2727 | 45 | -14.5014 | 8.0321 | 6.4693 | -10 | 10 | 10 | -205.4761 | -74.3121 | -48.2079 | -10 | 10 | 10 | 14.5014 | 6.4693 | -14.5014 | 8.0321 | 6.4693 | -14.5014 | -6.4693 | -65.582 | -13.0521 | -205.4761 | -74.3121 | -48.2079 | 65.582 | 13.0521 | 47.4199 | 47.4199 | 47.2817 | 47.2817 | 47.2817 | 46.974 | 46.974 | 42.097 | 42.097 | 40.198 | 42.2148 | 44.7188 | 45.0068 | 45.0068 | 50 | 42.2809 | 45.6897 | 40 | 46.2727 | 45
C-10 | 19186.5749 | -10368.8372 | -8148.4819 | -669.2558 | 63.7064 | 44.8053 | 63.5047 | 45.063 | 63.0554 | 45.0618 | 65 | 51.2953 | 54.8751 | 45 | 56.6407 | 45 | -14.5014 | 8.0321 | 6.4693 | -20 | 15 | 10 | -205.4761 | -74.3121 | -48.2079 | -20 | 15 | 10 | 14.5014 | 6.4693 | -14.5014 | 8.0321 | 6.4693 | -14.5014 | -6.4693 | -65.582 | -13.0521 | -205.4761 | -74.3121 | -48.2079 | 65.582 | 13.0521 | 63.7064 | 63.7064 | 63.5047 | 63.5047 | 63.5047 | 63.0554 | 63.0554 | 44.8053 | 44.8053 | 45.063 | 44.9338 | 44.7734 | 45.0618 | 45.0618 | 65 | 51.2953 | 54.8751 | 45 | 56.6407 | 45
ProsNet results:
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim
C-1 | 12830.88 | -6726.35 | -5477.61 | -626.92 | 58.06 | 45.52 | 57.88 | 46.08 | 57.48 | 45.4 | 65 | 46.6 | 54.65 | 45 | 52.86 | 45 | -14.67 | 8.17 | 6.5 | -10 | 10 | 10 | -200.96 | -76.86 | -48.85
C-2 | 11234.99 | -5786.38 | -4792.78 | -655.83 | 62.67 | 44.66 | 62.35 | 45.11 | 61.67 | 45.04 | 65 | 48.89 | 53.3 | 45 | 51.87 | 45 | -8.95 | 4.81 | 4.13 | -10 | 10 | 10 | -97.68 | -47.63 | -35.24
C-3 | 12801.22 | -6530.41 | -5639.74 | -631.06 | 58.74 | 45.28 | 58.54 | 45.73 | 58.13 | 45.37 | 65 | 46.64 | 54.36 | 45 | 53.09 | 45 | -13.65 | 7.31 | 6.34 | -10 | 10 | 10 | -217.52 | -108.97 | -82.21
C-4 | 11482.67 | -6660.93 | -4168.93 | -652.8 | 62.29 | 44.78 | 61.98 | 45.28 | 61.22 | 45.02 | 65 | 48.53 | 54.55 | 45 | 50.98 | 45 | -9.41 | 5.72 | 3.69 | -10 | 10 | 10 | -92.81 | -37.93 | -28.08
C-5 | 11423.48 | -5354.06 | -5414.57 | -654.85 | 62.43 | 44.68 | 62.12 | 45.07 | 61.52 | 45.09 | 65 | 48.62 | 52.68 | 45 | 52.76 | 45 | -9.23 | 4.5 | 4.73 | -10 | 10 | 10 | -94.74 | -41.76 | -26
C-6 | 11628.5 | -6236.82 | -4739.66 | -652.01 | 62.11 | 44.75 | 61.81 | 45.2 | 61.15 | 45.04 | 65 | 48.32 | 53.94 | 45 | 51.8 | 45 | -9.61 | 5.39 | 4.22 | -10 | 10 | 10 | -90.66 | -33.67 | -20.8
C-7 | 12854.49 | -6045.14 | -6179.02 | -630.33 | 58.41 | 45.33 | 58.23 | 45.53 | 57.87 | 45.68 | 65 | 46.57 | 53.67 | 45 | 53.86 | 45 | -14.09 | 6.83 | 7.27 | -10 | 10 | 10 | -210.45 | -95.22 | -60.93
C-8 | 12693.8 | -7147.21 | -4918.21 | -628.37 | 58.33 | 45.65 | 58.15 | 46.38 | 57.69 | 45.2 | 65 | 46.8 | 55.25 | 45 | 52.05 | 45 | -14.35 | 8.71 | 5.65 | -10 | 10 | 10 | -206.26 | -87.11 | -65.39
C-9 | 5052.54 | -3723.64 | -800.91 | -527.98 | 47.27 | 42.33 | 47.13 | 40.6 | 46.82 | 45.06 | 50 | 42.75 | 45.34 | 40 | 46.15 | 45 | -14.67 | 8.17 | 6.5 | -10 | 10 | 10 | -200.96 | -76.86 | -48.85
C-10 | 18425.31 | -10043.24 | -7715.08 | -666.98 | 63.22 | 45.21 | 63.02 | 45.4 | 62.58 | 45.56 | 65 | 51.79 | 54.6 | 45 | 56.06 | 45 | -14.67 | 8.17 | 6.5 | -20 | 15 | 10 | -200.96 | -76.86 | -48.85
| Err dotQ_1 | Err dotQ_2 | Err dotQ_3 | Err sum_dotQ_loss | Err T_1_prim_hot | Err T_1_prim_cold | Err T_2_prim_hot | Err T_2_prim_cold | Err T_3_prim_hot | Err T_3_prim_cold | Err T_1_sec_hot | Err T_1_sec_cold | Err T_2_sec_hot | Err T_2_sec_cold | Err T_3_sec_hot | Err T_3_sec_cold | Err dotV_1_prim | Err dotV_2_prim | Err dotV_3_prim | Err dotV_1_sec | Err dotV_2_sec | Err dotV_3_sec | Err Deltap_1_prim | Err Deltap_2_prim | Err Deltap_3_prim
C-01 | 6.7745 | 7.9628 | 6.0641 | 0.23187 | 0.39825 | -0.55804 | 0.39701 | -0.71891 | 0.39331 | -0.35596 | 0 | -1.1716 | 0.72422 | 0 | 0.43968 | 0 | -1.1489 | -1.6877 | -0.47183 | 0 | 0 | 0 | 2.2473 | -3.315 | -1.3145
C-02 | 7.8222 | 7.3605 | 9.2128 | 1.7336 | 1.0866 | -0.070454 | 1.0827 | -0.109 | 1.0754 | -0.039913 | 0 | -1.1954 | 0.57469 | 0 | 0.60761 | 0 | 0.88001 | 0.10227 | 2.0301 | 0 | 0 | 0 | 0.48788 | -0.66856 | 2.8276
C-03 | 6.9471 | 7.7183 | 6.7786 | 0.47453 | 0.5238 | -0.45739 | 0.5264 | -0.57759 | 0.51621 | -0.33435 | 0 | -1.1979 | 0.68921 | 0 | 0.51291 | 0 | -0.78285 | -1.1986 | -0.30344 | 0 | 0 | 0 | 1.5319 | -2.3116 | -0.82471
C-04 | 8.2583 | 8.3697 | 9.1033 | 1.7268 | 1.0816 | -0.16402 | 1.0849 | -0.26693 | 1.0801 | -0.019992 | 0 | -1.2885 | 0.76204 | 0 | 0.51777 | 0 | 0.62028 | -0.13203 | 1.7865 | 0 | 0 | 0 | 0.7481 | -0.90292 | 2.5239
C-05 | 7.8852 | 6.9115 | 9.6017 | 1.6543 | 1.0862 | -0.078275 | 1.0834 | -0.069704 | 1.0843 | -0.089038 | 0 | -1.2261 | 0.49729 | 0 | 0.7178 | 0 | 0.84781 | -0.1724 | 1.8184 | 0 | 0 | 0 | 0.51127 | -1.3823 | 2.7545
C-06 | 8.0406 | 7.455 | 9.6866 | 1.679 | 1.0738 | -0.1311 | 1.0746 | -0.19482 | 1.0702 | -0.039868 | 0 | -1.2679 | 0.63396 | 0 | 0.62682 | 0 | 0.59972 | -0.65407 | 2.2011 | 0 | 0 | 0 | 0.73099 | -1.908 | 3.0083
C-07 | 6.7911 | 6.309 | 7.9316 | 0.23379 | 0.47811 | -0.48724 | 0.46814 | -0.45646 | 0.46316 | -0.53522 | 0 | -1.1806 | 0.51075 | 0 | 0.66731 | 0 | -0.90576 | -1.3417 | -0.63252 | 0 | 0 | 0 | 1.808 | -2.6872 | -1.3436
C-08 | 6.9803 | 8.9161 | 5.008 | 0.40157 | 0.42582 | -0.55357 | 0.41958 | -0.7887 | 0.41339 | -0.19216 | 0 | -1.1998 | 0.87066 | 0 | 0.32788 | 0 | -1.0275 | -1.6226 | -0.2853 | 0 | 0 | 0 | 1.9998 | -2.9136 | -0.94117
C-09 | 6.9432 | 6.9599 | 11.2306 | 0.32344 | 0.14992 | -0.23304 | 0.15174 | -0.40196 | 0.15396 | -0.053247 | 0 | -0.46907 | 0.34972 | 0 | 0.12265 | 0 | -1.1489 | -1.6877 | -0.47183 | 0 | 0 | 0 | 2.2473 | -3.315 | -1.3145
C-10 | 4.1316 | 3.242 | 5.6176 | 0.34121 | 0.48644 | -0.4047 | 0.48473 | -0.33701 | 0.47542 | -0.49823 | 0 | -0.4947 | 0.27508 | 0 | 0.58069 | 0 | -1.1489 | -1.6877 | -0.47183 | 0 | 0 | 0 | 2.2473 | -3.315 | -1.3145

## Case_D
Case D |  | radial, 2 producers, 1 consumer at edge, equally dimensioned pumps (quadratic)
pump1 | type: NMT PLUS ER 25/40-180 |  |  | n_nom: 4100 |  | dotV_max: 55.33 l/min |  | Deltap_max: 402.21 hPa
for D-9: |  | T_1_sec_c = 40 °C |  | T_2_sec_h = 50 °C
for D-10: |  | dotV_1_sec = 15 l/min |  | dotV_2_sec = -20 l/min
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim | dotV_1 | dotV_2 | dotV_3 | dotV_1h_2h | dotV_2h_3h | dotV_1h_1c | dotV_2h_2c | dotV_3h_3c | dotV_1c_2c | dotV_2c_3c | Deltap_1h_2h | Deltap_2h_3h | Deltap_1h_1c | Deltap_2h_2c | Deltap_3h_3c | Deltap_1c_2c | Deltap_2c_3c | T_1h_2h | T_1h_1c | T_2h_1h | T_2h_3h | T_2h_2c | T_3h_2h | T_3h_3c | T_1c_1h | T_1c_2c | T_2c_2h | T_2c_1c | T_2c_3c | T_3c_3h | T_3c_2c | T_PSM1h | T_PSM1c | T_PSM2h | T_PSM2c | T_PSM3h | T_PSM3c
D-01 | -13047.6027 | 7992.158 | 5771.5713 | -716.1266 | 64.3799 | 49.8653 | 64.7388 | 49.6986 | 64.9966 | 49.2938 | 63.6394 | 45 | 65 | 53.5826 | 65 | 56.7549 | 12.8419 | -7.5912 | -5.2507 | 10 | -10 | -10 | -189.959 | -292.8204 | -310.0165 | 10 | -10 | -10 | -12.8419 | -5.2507 | 12.8419 | -7.5912 | -5.2507 | 12.8419 | 5.2507 | 51.4307 | 8.598 | -189.959 | -292.8204 | -310.0165 | -51.4307 | -8.598 | 64.3799 | 64.3799 | 64.6116 | 64.4276 | 64.7388 | 64.9966 | 64.9966 | 49.8653 | 49.8653 | 49.6986 | 49.6986 | 49.6986 | 49.2938 | 49.2938 | 63.6394 | 45 | 65 | 53.5826 | 65 | 56.7549
D-02 | -9448.9476 | 5908.9677 | 4216.495 | -676.5151 | 64.164 | 45.1784 | 64.9999 | 44.9149 | 65 | 44.2794 | 58.4985 | 45 | 65 | 56.5586 | 65 | 58.9764 | 7.1099 | -4.2028 | -2.907 | 10 | -10 | -10 | -103.1603 | -134.6896 | -139.9606 | 10 | -10 | -10 | -7.1099 | -2.907 | 7.1099 | -4.2028 | -2.907 | 7.1099 | 2.907 | 15.7647 | 2.6355 | -103.1603 | -134.6896 | -139.9606 | -15.7647 | -2.6355 | 64.164 | 64.164 | 64.5815 | 63.9766 | 64.9999 | 65 | 65 | 45.1784 | 45.1784 | 44.9149 | 44.9149 | 44.9149 | 44.2794 | 44.2794 | 58.4985 | 45 | 65 | 56.5586 | 65 | 58.9764
D-03 | -11067.0022 | 6867.1483 | 4882.7764 | -682.9225 | 64.3031 | 45.8362 | 64.9976 | 45.6129 | 65 | 45.073 | 60.81 | 45 | 65 | 55.1898 | 65 | 58.0246 | 8.5613 | -5.0608 | -3.5005 | 10 | -10 | -10 | -84.4262 | -130.1424 | -137.7851 | 10 | -10 | -10 | -8.5613 | -3.5005 | 8.5613 | -5.0608 | -3.5005 | 8.5613 | 3.5005 | 22.8581 | 3.8214 | -84.4262 | -130.1424 | -137.7851 | -22.8581 | -3.8214 | 64.3031 | 64.3031 | 64.6505 | 64.1487 | 64.9976 | 65 | 65 | 45.8362 | 45.8362 | 45.6129 | 45.6129 | 45.6129 | 45.073 | 45.073 | 60.81 | 45 | 65 | 55.1898 | 65 | 58.0246
D-06 | -12478.1344 | 7698.4757 | 5478.3744 | -698.7157 | 64.4146 | 47.6998 | 64.9557 | 47.5106 | 64.9998 | 47.052 | 62.8259 | 45 | 65 | 54.0022 | 65 | 57.1738 | 10.6648 | -6.3043 | -4.3606 | 10 | -10 | -10 | -232.1106 | -303.0517 | -314.9114 | 10 | -10 | -10 | -10.6648 | -4.3606 | 10.6648 | -6.3043 | -4.3606 | 10.6648 | 4.3606 | 35.4705 | 5.9299 | -232.1106 | -303.0517 | -314.9114 | -35.4705 | -5.9299 | 64.4146 | 64.4146 | 64.6939 | 64.3153 | 64.9557 | 64.9998 | 64.9998 | 47.6998 | 47.6998 | 47.5106 | 47.5106 | 47.5106 | 47.052 | 47.052 | 62.8259 | 45 | 65 | 54.0022 | 65 | 57.1738
D-09 | -10531.5976 | 3245.3842 | 7920.7502 | -634.5369 | 55.6428 | 43.9271 | 49.8939 | 43.7865 | 64.9953 | 43.4452 | 55.0451 | 40 | 50 | 45.3637 | 65 | 53.6846 | 12.8419 | -7.5912 | -5.2507 | 10 | -10 | -10 | -189.959 | -292.8204 | -310.0165 | 10 | -10 | -10 | -12.8419 | -5.2507 | 12.8419 | -7.5912 | -5.2507 | 12.8419 | 5.2507 | 51.4307 | 8.598 | -189.959 | -292.8204 | -310.0165 | -51.4307 | -8.598 | 55.6428 | 55.6428 | 55.8358 | 64.4263 | 49.8939 | 64.9953 | 64.9953 | 43.9271 | 43.9271 | 43.7865 | 43.7865 | 43.7865 | 43.4452 | 43.4452 | 55.0451 | 40 | 50 | 45.3637 | 65 | 53.6846
D-10 | -16099.9303 | 9843.7169 | 6947.2968 | -691.0834 | 64.5268 | 46.6168 | 64.989 | 46.4644 | 64.9959 | 46.0943 | 60.3333 | 45 | 65 | 57.9688 | 65 | 55.0753 | 12.8419 | -7.5912 | -5.2507 | 15 | -20 | -10 | -189.959 | -292.8204 | -310.0165 | 15 | -20 | -10 | -12.8419 | -5.2507 | 12.8419 | -7.5912 | -5.2507 | 12.8419 | 5.2507 | 51.4307 | 8.598 | -189.959 | -292.8204 | -310.0165 | -51.4307 | -8.598 | 64.5268 | 64.5268 | 64.7592 | 64.4269 | 64.989 | 64.9959 | 64.9959 | 46.6168 | 46.6168 | 46.4644 | 46.4644 | 46.4644 | 46.0943 | 46.0943 | 60.3333 | 45 | 65 | 57.9688 | 65 | 55.0753
ProsNet results:
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim
D-1 | -12101.09 | 7409.14 | 5407.31 | -715.36 | 63.88 | 50.43 | 64 | 50.26 | 64.86 | 49.85 | 62.35 | 45 | 65 | 54.38 | 65 | 57.25 | 12.9 | -7.73 | -5.17 | 10 | -10 | -10 | -189.72 | -287.57 | -306.06
D-2 | -8940.25 | 5572.19 | 4045.2 | -677.14 | 64.13 | 45.86 | 64.95 | 45.59 | 65 | 44.94 | 57.82 | 45 | 65 | 57.01 | 65 | 59.2 | 7.02 | -4.13 | -2.89 | 10 | -10 | -10 | -100.64 | -132.84 | -138.06
D-3 | -10267.22 | 6460.72 | 4492.78 | -686.29 | 64.2 | 46.83 | 64.84 | 46.6 | 64.99 | 46.03 | 59.72 | 45 | 65 | 55.74 | 65 | 58.56 | 8.48 | -5.08 | -3.4 | 10 | -10 | -10 | -82.63 | -127.99 | -136.07
D-4 | -9971.86 | 10416.09 | 129.69 | -573.77 | 61.89 | 47.6 | 62.17 | 47.36 | 40.8 | 65 | 59.3 | 45 | 65 | 50.06 | 65 | 64.81 | 10.01 | -10.09 | 0.08 | 10 | -10 | -10 | -203.18 | -264.61 | -264.54
D-5 | -9559.3 | 9.46 | 10225.07 | -675.22 | 62.1 | 47.09 | 62.4 | 65 | 62.73 | 46.77 | 58.71 | 45 | 65 | 64.99 | 65 | 50.34 | 9.13 | 0.05 | -9.19 | 10 | -10 | -10 | -169.56 | -221.55 | -274.09
D-6 | -11509.41 | 7169.04 | 5041.75 | -701.39 | 64.13 | 48.62 | 64.52 | 48.42 | 64.95 | 47.94 | 61.5 | 45 | 65 | 54.72 | 65 | 57.77 | 10.64 | -6.39 | -4.25 | 10 | -10 | -10 | -229.35 | -298.06 | -311.1
D-7 | -9730.99 | 8.48 | 10398 | -675.48 | 61.28 | 47.96 | 61.28 | 64.94 | 61.81 | 47.63 | 58.95 | 45 | 65 | 64.99 | 65 | 50.09 | 10.48 | 0.04 | -10.51 | 10 | -10 | -10 | -125.72 | -192.53 | -259.76
D-8 | -9845.56 | 10278.27 | 121.76 | -554.04 | 60.75 | 48.81 | 60.99 | 48.58 | 37.92 | 65 | 59.12 | 45 | 65 | 50.26 | 65 | 64.83 | 11.82 | -11.88 | 0.06 | 10 | -10 | -10 | -159.51 | -242.82 | -242.76
D-9 | -9786.42 | 2890.82 | 7529.11 | -633.51 | 55.27 | 44.39 | 49.61 | 44.25 | 64.8 | 43.9 | 54.03 | 40 | 50 | 45.85 | 65 | 54.2 | 12.9 | -7.73 | -5.17 | 10 | -10 | -10 | -189.72 | -287.57 | -306.06
D-10 | -15301.68 | 9518.31 | 6476.75 | -693.38 | 64.4 | 47.39 | 64.88 | 47.23 | 64.83 | 46.85 | 59.63 | 45 | 65 | 58.18 | 65 | 55.71 | 12.9 | -7.73 | -5.17 | 15 | -20 | -10 | -189.72 | -287.57 | -306.06
| Err dotQ_1 | Err dotQ_2 | Err dotQ_3 | Err sum_dotQ_loss | Err T_1_prim_hot | Err T_1_prim_cold | Err T_2_prim_hot | Err T_2_prim_cold | Err T_3_prim_hot | Err T_3_prim_cold | Err T_1_sec_hot | Err T_1_sec_cold | Err T_2_sec_hot | Err T_2_sec_cold | Err T_3_sec_hot | Err T_3_sec_cold | Err dotV_1_prim | Err dotV_2_prim | Err dotV_3_prim | Err dotV_1_sec | Err dotV_2_sec | Err dotV_3_sec | Err Deltap_1_prim | Err Deltap_2_prim | Err Deltap_3_prim
D-01 | 7.8217 | 7.8689 | 6.7365 | 0.10716 | 0.49986 | -0.56465 | 0.73883 | -0.56142 | 0.1366 | -0.55619 | 1.2894 | 0 | 0 | -0.79737 | 0 | -0.4951 | -0.45015 | -1.7955 | 1.5613 | 0 | 0 | 0 | 0.12595 | 1.8258 | 1.2927
D-02 | 5.69 | 6.0439 | 4.2345 | -0.092279 | 0.033966 | -0.68161 | 0.049907 | -0.67507 | -1.4207e-08 | -0.66064 | 0.6785 | 0 | 0 | -0.45138 | 0 | -0.22356 | 1.2802 | 1.7635 | 0.58945 | 0 | 0 | 0 | 2.5042 | 1.3924 | 1.3767
D-03 | 7.7897 | 6.2908 | 8.6805 | -0.49068 | 0.10308 | -0.99377 | 0.15763 | -0.98706 | 0.0099982 | -0.95696 | 1.09 | 0 | 0 | -0.55021 | 0 | -0.53539 | 0.95857 | -0.37784 | 2.9553 | 0 | 0 | 0 | 2.1738 | 1.6817 | 1.2605
D-06 | 8.4168 | 7.385 | 8.6602 | -0.38128 | 0.28455 | -0.92015 | 0.4357 | -0.90939 | 0.049831 | -0.88801 | 1.3259 | 0 | 0 | -0.71782 | 0 | -0.59625 | 0.23312 | -1.3419 | 2.6012 | 0 | 0 | 0 | 1.2037 | 1.6747 | 1.2251
D-09 | 7.6144 | 12.2652 | 5.2017 | 0.1621 | 0.37279 | -0.46285 | 0.28395 | -0.46346 | 0.19534 | -0.45476 | 1.0151 | 0 | 0 | -0.48626 | 0 | -0.51536 | -0.45015 | -1.7955 | 1.5613 | 0 | 0 | 0 | 0.12595 | 1.8258 | 1.2927
D-10 | 5.2167 | 3.4187 | 7.2652 | -0.33122 | 0.12681 | -0.77319 | 0.10901 | -0.76565 | 0.16591 | -0.7557 | 0.70327 | 0 | 0 | -0.21123 | 0 | -0.63471 | -0.45015 | -1.7955 | 1.5613 | 0 | 0 | 0 | 0.12595 | 1.8258 | 1.2927

## Case_E
Case E |  | meshed, 2 consumers, 1 producer, pump (quadratic)
pump1 | type: NMT PLUS ER 25/40-180 |  |  | n_nom: 4100 |  | dotV_max: 55.33 l/min |  | Deltap_max: 402.21 hPa
for E-9: |  | T_1_sec_c = 40 °C |  | T_3_sec_c = 50 °C
for E-10: |  | dotV_1_sec = 15 l/min |  | dotV_2_sec = -20 l/min
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim |  | dotV_1 | dotV_2 | dotV_3 | dotV_1h_2h | dotV_1h_3h | dotV_2h_3h | dotV_1h_1c | dotV_2h_2c | dotV_3h_3c | dotV_1c_2c | dotV_1c_3c | dotV_2c_3c | Deltap_1h_2h | Deltap_1h_3h | Deltap_2h_3h | Deltap_1h_1c | Deltap_2h_2c | Deltap_3h_3c | Deltap_1c_2c | Deltap_1c_3c | Deltap_2c_3c | T_1h_2h | T_1h_3h | T_1h_1c | T_2h_1h | T_2h_3h | T_2h_2c | T_3h_1h | T_3h_2h | T_3h_3c | T_1c_1h | T_1c_2c | T_1c_3c | T_2c_2h | T_2c_1c | T_2c_3c | T_3c_3h | T_3c_1c | T_3c_2c | T_PSM1h | T_PSM1c | T_PSM2h | T_PSM2c | T_PSM3h | T_PSM3c
E-01 | -6472.5345 | 13561.1063 | -6472.5345 | -616.0372 | 55.9619 | 45.6346 | 56.2411 | 45.4223 | 55.9619 | 45.6346 | 54.2465 | 45 | 65 | 45.627 | 54.2465 | 45 | 8.9534 | -17.9068 | 8.9534 | 10 | -10 | 10 | -92.3365 | -142.336 | -92.3365 |  | 10 | -10 | 10 | -8.9534 | 0 | 8.9534 | 8.9534 | -17.9068 | 8.9534 | 8.9534 | 0 | -8.9534 | 24.9998 | 0 | -24.9998 | -92.3365 | -142.336 | -92.3365 | -24.9998 | 0 | 24.9998 | 55.9619 | 1.85 | 55.9619 | 56.2411 | 56.2411 | 56.2411 | 1.85 | 55.9619 | 55.9619 | 45.6346 | 45.6346 | 1.85 | 45.4223 | 45.4223 | 45.4223 | 45.6346 | 1.85 | 45.6346 | 54.2465 | 45 | 65 | 45.627 | 54.2465 | 45
E-02 | -6239.7882 | 13134.9398 | -6239.7882 | -655.3634 | 61.492 | 45.0055 | 62.0136 | 44.6613 | 61.492 | 45.0055 | 53.914 | 45 | 65 | 46.2358 | 53.914 | 45 | 5.4068 | -10.8137 | 5.4068 | 10 | -10 | 10 | -59.6592 | -77.8932 | -59.6592 |  | 10 | -10 | 10 | -5.4068 | 0 | 5.4068 | 5.4068 | -10.8137 | 5.4068 | 5.4068 | 0 | -5.4068 | 9.117 | 0 | -9.117 | -59.6592 | -77.8932 | -59.6592 | -9.117 | 0 | 9.117 | 61.492 | 1.85 | 61.492 | 62.0136 | 62.0136 | 62.0136 | 1.85 | 61.492 | 61.492 | 45.0055 | 45.0055 | 1.85 | 44.6613 | 44.6613 | 44.6613 | 45.0055 | 1.85 | 45.0055 | 53.914 | 45 | 65 | 46.2358 | 53.914 | 45
E-03 | -7020.1125 | 13435.9506 | -5453.5457 | -962.2924 | 60.4184 | 45.0585 | 61.3112 | 44.5523 | 60.8233 | 45.0012 | 55.0287 | 45 | 65 | 45.8058 | 52.7908 | 45 | 6.5292 | -11.4532 | 4.924 | 10 | -10 | 10 | -49.1038 | -69.7465 | -49.4797 |  | 10 | -10 | 10 | -5.7529 | -0.77627 | 5.7003 | 6.5292 | -11.4532 | 4.924 | 5.7529 | 0.77627 | -5.7003 | 10.3213 | 0.18793 | -10.1334 | -49.1038 | -69.7465 | -49.4797 | -10.3213 | -0.18793 | 10.1334 | 60.8277 | 57.3853 | 60.4184 | 61.3112 | 61.3112 | 61.3112 | 60.8233 | 60.8233 | 60.8233 | 45.0585 | 45.0585 | 45.0585 | 44.5523 | 44.7344 | 44.3686 | 45.0012 | 42.7307 | 44.692 | 55.0287 | 45 | 65 | 45.8058 | 52.7908 | 45
E-04 | -6544.2712 | 13709.6155 | -6544.2713 | -621.0729 | 56.8753 | 45.348 | 57.1901 | 45.1158 | 56.8753 | 45.348 | 54.349 | 45 | 65 | 45.4148 | 54.349 | 45 | 8.1103 | -16.2205 | 8.1103 | 10 | -10 | 10 | -134.2333 | -175.2597 | -134.2333 |  | 10 | -10 | 10 | -8.1103 | -2.0002e-08 | 8.1103 | 8.1103 | -16.2205 | 8.1103 | 8.1103 | 0 | -8.1103 | 20.5132 | 0 | -20.5132 | -134.2333 | -175.2597 | -134.2333 | -20.5132 | 0 | 20.5132 | 56.8753 | 12 | 56.8753 | 57.1901 | 57.1901 | 57.1901 | 56.8753 | 56.8753 | 56.8753 | 45.348 | 45.348 | 1.85 | 45.1158 | 45.1158 | 45.1158 | 45.348 | 1.85 | 45.348 | 54.349 | 45 | 65 | 45.4148 | 54.349 | 45
E-05 | -5453.5457 | 13435.9506 | -7020.1125 | -962.2924 | 60.8233 | 45.0012 | 61.3112 | 44.5523 | 60.4184 | 45.0585 | 52.7908 | 45 | 65 | 45.8058 | 55.0287 | 45 | 4.924 | -11.4532 | 6.5292 | 10 | -10 | 10 | -49.4797 | -69.7465 | -49.1038 |  | 10 | -10 | 10 | -5.7003 | 0.77627 | 5.7529 | 4.924 | -11.4532 | 6.5292 | 5.7003 | -0.77627 | -5.7529 | 10.1334 | -0.18793 | -10.3213 | -49.4797 | -69.7465 | -49.1038 | -10.1334 | 0.18793 | 10.3213 | 60.8233 | 60.8233 | 60.8233 | 61.3112 | 61.3112 | 61.3112 | 57.3853 | 60.8277 | 60.4184 | 45.0012 | 44.692 | 42.7307 | 44.5523 | 44.3686 | 44.7344 | 45.0585 | 45.0585 | 45.0585 | 52.7908 | 45 | 65 | 45.8058 | 55.0287 | 45
E-06 | -5788.9583 | 13597.1611 | -6886.0542 | -922.1486 | 56.3484 | 45.1516 | 56.6433 | 45.3367 | 56.1002 | 46.0558 | 53.2699 | 45 | 65 | 45.5755 | 54.8372 | 45 | 7.386 | -17.1798 | 9.7938 | 10 | -10 | 10 | -111.3293 | -156.9296 | -110.4836 |  | 10 | -10 | 10 | -8.5504 | 1.1644 | 8.6293 | 7.386 | -17.1798 | 9.7938 | 8.5504 | -1.1644 | -8.6293 | 22.8001 | -0.42284 | -23.223 | -111.3293 | -156.9296 | -110.4836 | -22.8001 | 0.42284 | 23.223 | 56.3484 | 56.3484 | 56.3484 | 56.6433 | 56.6433 | 56.6433 | 54.2412 | 56.3511 | 56.1002 | 45.1516 | 45.0544 | 44.4377 | 45.3367 | 44.836 | 45.8329 | 46.0558 | 46.0558 | 46.0558 | 53.2699 | 45 | 65 | 45.5755 | 54.8372 | 45
E-07 | -6412.0282 | 13470.4891 | -6412.0282 | -646.4326 | 60.3661 | 45.0198 | 60.8276 | 44.7078 | 60.3661 | 45.0198 | 54.16 | 45 | 65 | 45.7564 | 54.16 | 45 | 5.9689 | -11.9378 | 5.9689 | 10 | -10 | 10 | -41.0384 | -63.2604 | -41.0384 |  | 10 | -10 | 10 | -5.9689 | 0 | 5.9689 | 5.9689 | -11.9378 | 5.9689 | 5.9689 | 0 | -5.9689 | 11.111 | 0 | -11.111 | -41.0384 | -63.2604 | -41.0384 | -11.111 | 0 | 11.111 | 60.3661 | 1.85 | 60.3661 | 60.8276 | 60.8276 | 60.8276 | 1.85 | 60.3661 | 60.3661 | 45.0198 | 45.0198 | 1.85 | 44.7078 | 44.7078 | 44.7078 | 45.0198 | 1.85 | 45.0198 | 54.16 | 45 | 65 | 45.7564 | 54.16 | 45
E-08 | -6886.0542 | 13597.1611 | -5788.9583 | -922.1486 | 56.1002 | 46.0558 | 56.6433 | 45.3367 | 56.3484 | 45.1516 | 54.8372 | 45 | 65 | 45.5755 | 53.2699 | 45 | 9.7938 | -17.1798 | 7.386 | 10 | -10 | 10 | -110.4836 | -156.9296 | -111.3293 |  | 10 | -10 | 10 | -8.6293 | -1.1644 | 8.5504 | 9.7938 | -17.1798 | 7.386 | 8.6293 | 1.1644 | -8.5504 | 23.223 | 0.42284 | -22.8001 | -110.4836 | -156.9296 | -111.3293 | -23.223 | -0.42284 | 22.8001 | 56.3511 | 54.2412 | 56.1002 | 56.6433 | 56.6433 | 56.6433 | 56.3484 | 56.3484 | 56.3484 | 46.0558 | 46.0558 | 46.0558 | 45.3367 | 45.8329 | 44.836 | 45.1516 | 44.4377 | 45.0544 | 54.8372 | 45 | 65 | 45.5755 | 53.2699 | 45
E-09 | -9424.8103 | 13561.1063 | -3520.2588 | -616.0372 | 55.9619 | 40.924 | 56.2411 | 45.4223 | 55.9619 | 50.3451 | 53.464 | 40 | 65 | 45.627 | 55.0289 | 50 | 8.9534 | -17.9068 | 8.9534 | 10 | -10 | 10 | -92.3365 | -142.336 | -92.3365 |  | 10 | -10 | 10 | -8.9534 | 0 | 8.9534 | 8.9534 | -17.9068 | 8.9534 | 8.9534 | 0 | -8.9534 | 24.9998 | 0 | -24.9998 | -92.3365 | -142.336 | -92.3365 | -24.9998 | 0 | 24.9998 | 55.9619 | 1.85 | 55.9619 | 56.2411 | 56.2411 | 56.2411 | 1.85 | 55.9619 | 55.9619 | 40.924 | 40.924 | 1.85 | 45.4223 | 40.7415 | 50.1031 | 50.3451 | 1.85 | 50.3451 | 53.464 | 40 | 65 | 45.627 | 55.0289 | 50
E-10 | -10520.8968 | 21184.4438 | -10000.4925 | -663.0545 | 61.9369 | 45.1501 | 62.2541 | 45.3535 | 61.9369 | 45.9805 | 55.0199 | 45 | 65 | 49.8683 | 59.2864 | 45 | 8.9534 | -17.9068 | 8.9534 | 15 | -20 | 10 | -92.3365 | -142.336 | -92.3365 |  | 15 | -20 | 10 | -8.9534 | 0 | 8.9534 | 8.9534 | -17.9068 | 8.9534 | 8.9534 | 0 | -8.9534 | 24.9998 | 0 | -24.9998 | -92.3365 | -142.336 | -92.3365 | -24.9998 | 0 | 24.9998 | 61.9369 | 1.85 | 61.9369 | 62.2541 | 62.2541 | 62.2541 | 1.85 | 61.9369 | 61.9369 | 45.1501 | 45.1501 | 1.85 | 45.3535 | 44.9409 | 45.766 | 45.9805 | 1.85 | 45.9805 | 55.0199 | 45 | 65 | 49.8683 | 59.2864 | 45
ProsNet results:
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim | dotV_bypass_h
E-1 | -6097.56 | 12814.88 | -6097.56 | -619.84 | 56.05 | 46.26 | 56.33 | 46.04 | 56.05 | 46.26 | 53.74 | 45 | 65 | 46.62 | 53.74 | 45 | 8.93 | -17.86 | 8.93 | 10 | -10 | 10 | -91.57 | -141.44 | -91.57 | 0
E-2 | -5752.83 | 12152.18 | -5752.83 | -646.6 | 60.63 | 45.18 | 61.15 | 44.83 | 60.63 | 45.18 | 53.25 | 45 | 65 | 47.57 | 53.25 | 45 | 5.34 | -10.68 | 5.34 | 10 | -10 | 10 | -58.49 | -78.11 | -58.49 | 0
E-3 | -6403.27 | 12430.85 | -5085.05 | -942.53 | 59.7 | 45.45 | 60.58 | 44.81 | 60.09 | 45.1 | 54.18 | 45 | 65 | 47.17 | 52.29 | 45 | 6.44 | -11.31 | 4.86 | 10 | -10 | 10 | -47.98 | -70.08 | -48.66 | 0.74
E-4 | -6134 | 12891.37 | -6134 | -623.46 | 56.83 | 45.95 | 57.15 | 45.71 | 56.83 | 45.95 | 53.8 | 45 | 65 | 46.51 | 53.8 | 45 | 8.08 | -16.16 | 8.08 | 10 | -10 | 10 | -133.02 | -174.6 | -133.02 | 0
E-5 | -5085.05 | 12430.85 | -6403.27 | -942.53 | 60.09 | 45.1 | 60.58 | 44.81 | 59.7 | 45.45 | 52.29 | 45 | 65 | 47.17 | 54.18 | 45 | 4.86 | -11.31 | 6.44 | 10 | -10 | 10 | -48.66 | -70.08 | -47.98 | -0.74
E-6 | -5507.59 | 12862.11 | -6434.68 | -919.83 | 56.36 | 45.63 | 56.66 | 45.89 | 56.12 | 46.67 | 52.9 | 45 | 65 | 46.56 | 54.23 | 45 | 7.36 | -17.13 | 9.77 | 10 | -10 | 10 | -110.49 | -156.15 | -109.39 | -1.15
E-7 | -5933.79 | 12508.05 | -5933.79 | -640.54 | 59.73 | 45.29 | 60.19 | 44.97 | 59.73 | 45.29 | 53.51 | 45 | 65 | 47.06 | 53.51 | 45 | 5.89 | -11.78 | 5.89 | 10 | -10 | 10 | -40.22 | -63.67 | -40.22 | 0
E-8 | -6434.68 | 12862.11 | -5507.59 | -919.83 | 56.12 | 46.67 | 56.66 | 45.89 | 56.36 | 45.63 | 54.23 | 45 | 65 | 46.56 | 52.9 | 45 | 9.77 | -17.13 | 7.36 | 10 | -10 | 10 | -109.39 | -156.15 | -110.49 | 1.15
E-9 | -8856.46 | 12814.88 | -3338.65 | -619.84 | 56.05 | 41.83 | 56.33 | 46.04 | 56.05 | 50.69 | 52.7 | 40 | 65 | 46.62 | 54.79 | 50 | 8.93 | -17.86 | 8.93 | 10 | -10 | 10 | -91.57 | -141.44 | -91.57 | 0
E-10 | -10079.7 | 19980.39 | -9236.02 | -664.76 | 61.74 | 45.55 | 62.06 | 46.01 | 61.74 | 46.9 | 54.64 | 45 | 65 | 50.67 | 58.24 | 45 | 8.93 | -17.86 | 8.93 | 15 | -20 | 10 | -91.57 | -141.44 | -91.57 | 0
| Err dotQ_1 | Err dotQ_2 | Err dotQ_3 | Err sum_dotQ_loss | Err T_1_prim_hot | Err T_1_prim_cold | Err T_2_prim_hot | Err T_2_prim_cold | Err T_3_prim_hot | Err T_3_prim_cold | Err T_1_sec_hot | Err T_1_sec_cold | Err T_2_sec_hot | Err T_2_sec_cold | Err T_3_sec_hot | Err T_3_sec_cold | Err dotV_1_prim | Err dotV_2_prim | Err dotV_3_prim | Err dotV_1_sec | Err dotV_2_sec | Err dotV_3_sec | Err Deltap_1_prim | Err Deltap_2_prim | Err Deltap_3_prim
E-01 | 6.1496 | 5.8231 | 6.1496 | -0.61351 | -0.088059 | -0.62542 | -0.088859 | -0.61768 | -0.088059 | -0.62542 | 0.50648 | 0 | 0 | -0.99301 | 0.50648 | 0 | 0.26182 | 0.26182 | 0.26182 | 0 | 0 | 0 | 0.83703 | 0.63349 | 0.83703
E-02 | 8.4647 | 8.0871 | 8.4647 | 1.3553 | 0.86197 | -0.17449 | 0.86355 | -0.1687 | 0.86197 | -0.17449 | 0.66398 | 0 | 0 | -1.3342 | 0.66398 | 0 | 1.2519 | 1.2519 | 1.2519 | 0 | 0 | 0 | 1.9991 | -0.27758 | 1.9991
E-03 | 9.6332 | 8.0855 | 7.2466 | 2.0967 | 0.71843 | -0.39145 | 0.73119 | -0.25766 | 0.73327 | -0.098752 | 0.84873 | 0 | 0 | -1.3642 | 0.50078 | 0 | 1.3847 | 1.266 | 1.3171 | 0 | 0 | 0 | 2.3423 | -0.47592 | 1.6845
E-04 | 6.6885 | 6.3472 | 6.6885 | -0.38288 | 0.045342 | -0.60196 | 0.040075 | -0.59422 | 0.045342 | -0.60196 | 0.54896 | 0 | 0 | -1.0952 | 0.54896 | 0 | 0.37467 | 0.37467 | 0.37467 | 0 | 0 | 0 | 0.91212 | 0.37781 | 0.91212
E-05 | 7.2466 | 8.0855 | 9.6332 | 2.0967 | 0.73327 | -0.098752 | 0.73119 | -0.25766 | 0.71843 | -0.39145 | 0.50078 | 0 | 0 | -1.3642 | 0.84873 | 0 | 1.3171 | 1.266 | 1.3847 | 0 | 0 | 0 | 1.6845 | -0.47592 | 2.3423
E-06 | 5.1087 | 5.7149 | 7.0147 | 0.25207 | -0.011625 | -0.47838 | -0.016653 | -0.55327 | -0.019781 | -0.61416 | 0.36994 | 0 | 0 | -0.98452 | 0.60722 | 0 | 0.35345 | 0.29056 | 0.24318 | 0 | 0 | 0 | 0.75963 | 0.49925 | 0.99976
E-07 | 8.0596 | 7.6946 | 8.0596 | 0.91995 | 0.63607 | -0.27016 | 0.63756 | -0.26224 | 0.63607 | -0.27016 | 0.65004 | 0 | 0 | -1.3036 | 0.65004 | 0 | 1.3399 | 1.3399 | 1.3399 | 0 | 0 | 0 | 2.0349 | -0.64324 | 2.0349
E-08 | 7.0147 | 5.7149 | 5.1087 | 0.25207 | -0.019781 | -0.61416 | -0.016653 | -0.55327 | -0.011625 | -0.47838 | 0.60722 | 0 | 0 | -0.98452 | 0.36994 | 0 | 0.24318 | 0.29056 | 0.35345 | 0 | 0 | 0 | 0.99976 | 0.49925 | 0.75963
E-09 | 6.4174 | 5.8231 | 5.4396 | -0.61351 | -0.088059 | -0.90597 | -0.088859 | -0.61768 | -0.088059 | -0.34487 | 0.76401 | 0 | 0 | -0.99301 | 0.23894 | 0 | 0.26182 | 0.26182 | 0.26182 | 0 | 0 | 0 | 0.83703 | 0.63349 | 0.83703
E-10 | 4.3771 | 6.0262 | 8.2771 | -0.25656 | 0.19692 | -0.39987 | 0.19407 | -0.65653 | 0.19692 | -0.91953 | 0.3799 | 0 | 0 | -0.80175 | 1.0464 | 0 | 0.26182 | 0.26182 | 0.26182 | 0 | 0 | 0 | 0.83703 | 0.63349 | 0.83703

## Case_F
Case F |  | meshed, 2 producers, 1 consumer, equally dimensioned pumps (quadratic)
pump1 | type: NMT PLUS ER 25/40-180 |  |  | n_nom: 4100 |  | dotV_max: 55.33 l/min |  | Deltap_max: 402.21 hPa
for F-9: |  | T_1_sec_h = 50 °C |  | T_2_sec_c = 40 °C
for F-10: |  | dotV_1_sec = -20 l/min |  | dotV_2_sec = 15 l/min
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim |  | dotV_1 | dotV_2 | dotV_3 | dotV_1h_2h | dotV_1h_3h | dotV_2h_3h | dotV_1h_1c | dotV_2h_2c | dotV_3h_3c | dotV_1c_2c | dotV_1c_3c | dotV_2c_3c | Deltap_1h_2h | Deltap_1h_3h | Deltap_2h_3h | Deltap_1h_1c | Deltap_2h_2c | Deltap_3h_3c | Deltap_1c_2c | Deltap_1c_3c | Deltap_2c_3c | T_1h_2h | T_1h_3h | T_1h_1c | T_2h_1h | T_2h_3h | T_2h_2c | T_3h_1h | T_3h_2h | T_3h_3c | T_1c_1h | T_1c_2c | T_1c_3c | T_2c_2h | T_2c_1c | T_2c_3c | T_3c_3h | T_3c_1c | T_3c_2c | T_PSM1h | T_PSM1c | T_PSM2h | T_PSM2c | T_PSM3h | T_PSM3c
F-01 | 7015.4034 | -13299.4536 | 7015.4034 | -731.3532 | 64.7934 | 51.4175 | 64.3955 | 51.7169 | 64.7934 | 51.4175 | 65 | 54.978 | 63.9992 | 45 | 65 | 54.978 | -7.4926 | 14.9852 | -7.4926 | -10 | 10 | -10 | -293.6715 | -258.6563 | -293.6715 |  | -10 | 10 | -10 | 7.4926 | 0 | -7.4926 | -7.4926 | 14.9852 | -7.4926 | -7.4926 | 0 | 7.4926 | -17.5076 | 0 | 17.5076 | -293.6715 | -258.6563 | -293.6715 | 17.5076 | 0 | -17.5076 | 64.7934 | 1.85 | 64.7934 | 64.3955 | 64.3955 | 64.3955 | 1.85 | 64.7934 | 64.7934 | 51.4175 | 51.4175 | 1.85 | 51.7169 | 51.7169 | 51.7169 | 51.4175 | 1.85 | 51.4175 | 65 | 54.978 | 63.9992 | 45 | 65 | 54.978
F-02 | 5516.3873 | -10351.7148 | 5516.3873 | -681.0599 | 65 | 44.9649 | 64.2417 | 45.4434 | 65 | 44.9649 | 65 | 57.1194 | 59.7882 | 45 | 65 | 57.1194 | -3.9334 | 7.8668 | -3.9334 | -10 | 10 | -10 | -135.9439 | -126.2939 | -135.9439 |  | -10 | 10 | -10 | 3.9334 | -2.2223e-08 | -3.9334 | -3.9334 | 7.8668 | -3.9334 | -3.9334 | 0 | 3.9334 | -4.825 | 0 | 4.825 | -135.9439 | -126.2939 | -135.9439 | 4.825 | 0 | -4.825 | 65 | 12 | 65 | 64.2417 | 64.2417 | 64.2417 | 65 | 65 | 65 | 44.9649 | 44.9649 | 1.85 | 45.4434 | 45.4434 | 45.4434 | 44.9649 | 1.85 | 44.9649 | 65 | 57.1194 | 59.7882 | 45 | 65 | 57.1194
F-04 | 6417.8278 | -12151.7245 | 6417.8278 | -694.6754 | 64.9982 | 46.6434 | 64.4002 | 47.0388 | 64.9982 | 46.6434 | 65 | 55.8317 | 62.3596 | 45 | 65 | 55.8317 | -4.9951 | 9.9901 | -4.9951 | -10 | 10 | -10 | -130.5206 | -114.9584 | -130.5206 |  | -10 | 10 | -10 | 4.9951 | 0 | -4.9951 | -4.9951 | 9.9901 | -4.9951 | -4.9951 | 0 | 4.9951 | -7.7811 | 0 | 7.7811 | -130.5206 | -114.9584 | -130.5206 | 7.7811 | 0 | -7.7811 | 64.9982 | 1.85 | 64.9982 | 64.4002 | 64.4002 | 64.4002 | 1.85 | 64.9982 | 64.9982 | 46.6434 | 46.6434 | 1.85 | 47.0388 | 47.0388 | 47.0388 | 46.6434 | 1.85 | 46.6434 | 65 | 55.8317 | 62.3596 | 45 | 65 | 55.8317
F-07 | 6801.5293 | -12893.4804 | 6801.5291 | -709.578 | 64.9817 | 48.5133 | 64.4751 | 48.8658 | 64.9817 | 48.5133 | 65 | 55.2835 | 63.4193 | 45 | 65 | 55.2835 | -5.9001 | 11.8002 | -5.9001 | -10 | 10 | -10 | -305.8738 | -284.1614 | -305.8738 |  | -10 | 10 | -10 | 5.9001 | 0 | -5.9001 | -5.9001 | 11.8002 | -5.9001 | -5.9001 | -4.0257e-08 | 5.9001 | -10.8562 | 0 | 10.8562 | -305.8738 | -284.1614 | -305.8738 | 10.8562 | 0 | -10.8562 | 64.9817 | 1.85 | 64.9817 | 64.4751 | 64.4751 | 64.4751 | 1.85 | 64.9817 | 64.9817 | 48.5133 | 48.5133 | 12 | 48.8658 | 48.8658 | 48.8658 | 48.5133 | 48.5133 | 48.5133 | 65 | 55.2835 | 63.4193 | 45 | 65 | 55.2835
F-09 | 2260.0937 | -11641.6359 | 10007.6609 | -626.1187 | 49.9334 | 45.6243 | 56.9778 | 45.8796 | 64.7053 | 45.6243 | 50 | 46.7713 | 56.6309 | 40 | 65 | 50.7033 | -7.4926 | 14.9852 | -7.4926 | -10 | 10 | -10 | -293.6715 | -258.6563 | -293.6715 |  | -10 | 10 | -10 | 7.4926 | 0 | -7.4926 | -7.4926 | 14.9852 | -7.4926 | -7.4926 | 0 | 7.4926 | -17.5076 | 0 | 17.5076 | -293.6715 | -258.6563 | -293.6715 | 17.5076 | 0 | -17.5076 | 49.9334 | 1.85 | 49.9334 | 49.6476 | 64.3081 | 56.9778 | 1.85 | 64.7053 | 64.7053 | 45.6243 | 45.6243 | 1.85 | 45.8796 | 45.8796 | 45.8796 | 45.6243 | 1.85 | 45.6243 | 50 | 46.7713 | 56.6309 | 40 | 65 | 50.7033
F-10 | 9097.9326 | -17374.8617 | 8964.1865 | -701.8529 | 64.991 | 47.6445 | 64.4651 | 47.9152 | 64.736 | 47.6445 | 65 | 58.5015 | 61.5475 | 45 | 65 | 52.194 | -7.4926 | 14.9852 | -7.4926 | -20 | 15 | -10 | -293.6715 | -258.6563 | -293.6715 |  | -20 | 15 | -10 | 7.4926 | 0 | -7.4926 | -7.4926 | 14.9852 | -7.4926 | -7.4926 | 0 | 7.4926 | -17.5076 | 0 | 17.5076 | -293.6715 | -258.6563 | -293.6715 | 17.5076 | 0 | -17.5076 | 64.991 | 1.85 | 64.991 | 64.5917 | 64.3386 | 64.4651 | 1.85 | 64.736 | 64.736 | 47.6445 | 47.6445 | 1.85 | 47.9152 | 47.9152 | 47.9152 | 47.6445 | 1.85 | 47.6445 | 65 | 58.5015 | 61.5475 | 45 | 65 | 52.194
ProsNet results:
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim | dotV_bypass_h
F-1 | 6577.35 | -12429.32 | 6577.35 | -725.46 | 64.21 | 51.58 | 63.82 | 51.88 | 64.21 | 51.58 | 65 | 55.57 | 62.82 | 45 | 65 | 55.57 | -7.47 | 14.94 | -7.47 | -10 | 10 | -10 | -289.77 | -253.75 | -289.77 | 0
F-2 | 5184.07 | -9685.34 | 5184.07 | -682.86 | 64.97 | 45.83 | 64.2 | 46.32 | 64.97 | 45.83 | 65 | 57.57 | 58.89 | 45 | 65 | 57.57 | -3.88 | 7.77 | -3.88 | -10 | 10 | -10 | -133.95 | -122.96 | -133.95 | 0
F-3 | 10531.91 | -9545.58 | 18.42 | -1004.74 | 61.62 | 47.56 | 60.84 | 48.02 | 61 | 65 | 65 | 49.9 | 58.69 | 45 | 65 | 64.97 | -10.74 | 10.68 | 0.07 | -10 | 10 | -10 | -257.05 | -231.05 | -245.13 | -4.51
F-4 | 5971.21 | -11245.63 | 5971.21 | -696.86 | 64.87 | 47.53 | 64.27 | 47.94 | 64.87 | 47.53 | 65 | 56.44 | 61.13 | 45 | 65 | 56.44 | -4.94 | 9.87 | -4.94 | -10 | 10 | -10 | -128.77 | -111.73 | -128.77 | 0
F-5 | 18.42 | -9545.58 | 10531.91 | -1004.74 | 61 | 65 | 60.84 | 48.02 | 61.62 | 47.56 | 65 | 64.97 | 58.69 | 45 | 65 | 49.9 | 0.07 | 10.68 | -10.74 | -10 | 10 | -10 | -245.13 | -231.05 | -257.05 | 4.51
F-6 | 16.76 | -9401.49 | 10390.37 | -1005.64 | 59.75 | 64.99 | 59.66 | 49.24 | 60.29 | 48.81 | 65 | 64.98 | 58.48 | 45 | 65 | 50.1 | 0.05 | 12.94 | -12.98 | -10 | 10 | -10 | -210.88 | -190.85 | -227.5 | 5.44
F-7 | 6338.41 | -11967.32 | 6338.41 | -709.56 | 64.7 | 49.2 | 64.19 | 49.56 | 64.7 | 49.2 | 65 | 55.91 | 62.16 | 45 | 65 | 55.91 | -5.87 | 11.73 | -5.87 | -10 | 10 | -10 | -301.66 | -278.4 | -301.66 | 0
F-8 | 10390.37 | -9401.49 | 16.76 | -1005.64 | 60.29 | 48.81 | 59.66 | 49.24 | 59.75 | 64.99 | 65 | 50.1 | 58.48 | 45 | 65 | 64.98 | -12.98 | 12.94 | 0.05 | -10 | 10 | -10 | -227.5 | -190.85 | -210.88 | -5.44
F-9 | 2074.41 | -10880.38 | 9426.91 | -621.02 | 49.75 | 45.77 | 56.47 | 46.03 | 63.87 | 45.77 | 50 | 47.03 | 55.6 | 40 | 65 | 51.48 | -7.47 | 14.94 | -7.47 | -10 | 10 | -10 | -289.77 | -253.75 | -289.77 | 0
F-10 | 8760.31 | -16350.95 | 8290.22 | -699.65 | 64.91 | 48.09 | 64.06 | 48.36 | 64 | 48.09 | 65 | 58.72 | 60.63 | 45 | 65 | 53.11 | -7.47 | 14.94 | -7.47 | -20 | 15 | -10 | -289.77 | -253.75 | -289.77 | 0
| Err dotQ_1 | Err dotQ_2 | Err dotQ_3 | Err sum_dotQ_loss | Err T_1_prim_hot | Err T_1_prim_cold | Err T_2_prim_hot | Err T_2_prim_cold | Err T_3_prim_hot | Err T_3_prim_cold | Err T_1_sec_hot | Err T_1_sec_cold | Err T_2_sec_hot | Err T_2_sec_cold | Err T_3_sec_hot | Err T_3_sec_cold | Err dotV_1_prim | Err dotV_2_prim | Err dotV_3_prim | Err dotV_1_sec | Err dotV_2_sec | Err dotV_3_sec | Err Deltap_1_prim | Err Deltap_2_prim | Err Deltap_3_prim
F-01 | 6.66 | 7.0007 | 6.66 | 0.81234 | 0.58342 | -0.16246 | 0.57554 | -0.16313 | 0.58342 | -0.16246 | 0 | -0.592 | 1.1792 | 0 | 0 | -0.592 | 0.30241 | 0.30241 | 0.30241 | 0 | 0 | 0 | 1.3464 | 1.9335 | 1.3464
F-02 | 6.4104 | 6.8802 | 6.4104 | -0.26362 | 0.029976 | -0.86506 | 0.041687 | -0.87657 | 0.029976 | -0.86506 | 0 | -0.45055 | 0.89816 | 0 | 0 | -0.45055 | 1.3759 | 1.2455 | 1.3759 | 0 | 0 | 0 | 1.4885 | 2.7114 | 1.4885
F-04 | 7.4795 | 8.0573 | 7.4795 | -0.31349 | 0.12818 | -0.88661 | 0.13016 | -0.90125 | 0.12818 | -0.88661 | 0 | -0.60833 | 1.2296 | 0 | 0 | -0.60833 | 1.1146 | 1.217 | 1.1146 | 0 | 0 | 0 | 1.3595 | 2.8894 | 1.3595
F-07 | 7.3066 | 7.7391 | 7.3066 | 0.0025383 | 0.28167 | -0.6867 | 0.2851 | -0.69422 | 0.28167 | -0.6867 | 0 | -0.62647 | 1.2593 | 0 | 0 | -0.62647 | 0.51244 | 0.59812 | 0.51244 | 0 | 0 | 0 | 1.3969 | 2.0695 | 1.3969
F-09 | 8.9512 | 6.9966 | 6.1606 | 0.82102 | 0.18345 | -0.14575 | 0.50783 | -0.15041 | 0.83531 | -0.14575 | 0 | -0.25871 | 1.0309 | 0 | 0 | -0.77666 | 0.30241 | 0.30241 | 0.30241 | 0 | 0 | 0 | 1.3464 | 1.9335 | 1.3464
F-10 | 3.854 | 6.2621 | 8.1297 | 0.31486 | 0.081047 | -0.44549 | 0.40513 | -0.44481 | 0.73604 | -0.44549 | 0 | -0.21852 | 0.91749 | 0 | 0 | -0.91598 | 0.30241 | 0.30241 | 0.30241 | 0 | 0 | 0 | 1.3464 | 1.9335 | 1.3464