## standard_case
configuration
No of prosumers |  | 3
substations |  | hydraulic: | pipe + heat exchanger |  |  | thermal: | only heat exchanger
parametrization
fluid |  | rho=1000
(water) |  | cp=4200
mu=1.0016*(10**(-3))
valve |  | K_vs=2.5
heat exchanger |  | dotV_nom=21.504 |  | Deltap_nom=155
|  | k_nom = 5270 |  | A = 1.13
pipe1 |  | L=15 | d_hy=0.022 | epsilon=0.011 | u_nom=0.5 | zeta_instal=10 | N_layers = 2 | d_layers = [0.022, 0.024, 0.062] | lambda_layers = [395, 0.04] | h_ir=3500 | h_or=float('inf')
pipe2 |  | L=5 | d_hy=0.022 | epsilon=0.011 | u_nom=0.5 | zeta_instal=3.5 | N_layers = 2 | d_layers = [0.022, 0.024, 0.062] | lambda_layers = [395, 0.04] | h_ir=3500 | h_or=float('inf')
Scenario
T_soil |  | 12 °C
participation prosumers |  | pi: 1
T_in_sec | for producers | 65 °C
T_in_sec | for consumers | 45 °C
dotV_sec | for producers | -10 l/min
dotV_sec | for consumers | 10 l/min

## variation possibilities
configuration
topology | radial
mesh
pump model | quadratic
linear
parametrization
pump dimensioning | pump1 | type: NMT PLUS ER 25/40-180 | n_nom: 4100 | dotV_max: 55.33 l/min | Deltap_max: 402.21 hPa
| pump2 | type: NMT PLUS ER 25/60-180 | n_nom: 4100 | dotV_max: 55.17 l/min | Deltap_max: 565.06 hPa
| pump3 | type: NMT PLUS ER 25/80-180 | n_nom: 4800 | dotV_max: 57.67 l/min | Deltap_max: 751.45 hPa
scenario
mu‘s for each prosumer (mode) | producer (1) or consumer (-1)
kappa for consumers | Kappa: 0.6
Kappa. 0.9
u for producers | U: 0.6
U: 0.9

## Cases overview
Base cases
For each base case (letters), scenarios (numbers) with different control inputs are calculated. All combinations of the options for kappa and u for all prosumers are calculated. Two options for kappa (0.6 and 0.9) and two options for u (0.6 and 0.9) lead for 3 prosumers to 8 scenarios for each base case (see table on the right). 2 additional scenarios result from using different volume flow and different inlet temperatures at the secondary side.
|  |  | X-1 | X-2 | X-3 | X-4 | X-5 | X-6 | X-7 | X-8 | X-9 | X-10
|  | prosumer1 | 0.9 | 0.6 | 0.9 | 0.6 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9
|  | prosumer2 | 0.9 | 0.6 | 0.6 | 0.9 | 0.6 | 0.9 | 0.6 | 0.9 | 0.9 | 0.9
|  | prosumer3 | 0.9 | 0.6 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.6 | 0.9 | 0.9
[11 empty] | dotV_sec | T_sec_in
For cases with equally dimensioned pumps, pump1 is used. For cases with differently dimensioned cases pump3 is used as big pump.
Base case A | radial, 2 consumers, 1 producer in center, pump (quadratic)
Base case B | radial, 2 producers, 1 consumer in center, equally dimensioned pumps (quadratic)
Base case C | radial, 2 consumers, 1 producer at edge, pump (quadratic)
Base case D | radial, 2 producers, 1 consumer at edge, equally dimensioned pumps (quadratic)
Base case E | meshed, 2 consumers, 1 producer, pump (quadratic)
Base case F | meshed, 2 producers, 1 consumer, equally dimensioned pumps (quadratic)
(Base case G) | radial, 2 producers, 1 consumer in center, differently dimensioned pumps (quadratic)
(Base case H) | radial, 2 producers, 1 consumer at edge, differently dimensioned pumps (quadratic)
(Base case I) | meshed, 2 producers, 1 consumer, differently dimensioned pumps (quadratic)
((Base case J)) | radial, 2 producers, 1 consumer in center, equally dimensioned pumps (linear)
((Base case K)) | radial, 2 producers, 1 consumer in center, differently dimensioned pumps (linear)
lin
lin
lin
lin

## Case_A
Case A |  | radial, 2 consumers, 1 producer in center, pump (quadratic)
pump1 | type: NMT PLUS ER 25/40-180 |  |  | n_nom: 4100 |  | dotV_max: 55.33 l/min |  | Deltap_max: 402.21 hPa
for A-9: |  | T_1_sec_c = 40 °C |  | T_3_sec_c = 50 °C
for A-10: |  | dotV_1_sec = 15 l/min |  | dotV_2_sec = -20 l/min
| dotQ_1 | dotQ_2 | dotQ_3 | sum_dotQ_loss | T_1_prim_hot | T_1_prim_cold | T_2_prim_hot | T_2_prim_cold | T_3_prim_hot | T_3_prim_cold | T_1_sec_hot | T_1_sec_cold | T_2_sec_hot | T_2_sec_cold | T_3_sec_hot | T_3_sec_cold | dotV_1_prim | dotV_2_prim | dotV_3_prim | dotV_1_sec | dotV_2_sec | dotV_3_sec | Deltap_1_prim | Deltap_2_prim | Deltap_3_prim | dotV_1 | dotV_2 | dotV_3 | dotV_1h_2h | dotV_2h_3h | dotV_1h_1c | dotV_2h_2c | dotV_3h_3c | dotV_1c_2c | dotV_2c_3c | Deltap_1h_2h | Deltap_2h_3h | Deltap_1h_1c | Deltap_2h_2c | Deltap_3h_3c | Deltap_1c_2c | Deltap_2c_3c | T_1h_2h | T_1h_1c | T_2h_1h | T_2h_3h | T_2h_2c | T_3h_2h | T_3h_3c | T_1c_1h | T_1c_2c | T_2c_2h | T_2c_1c | T_2c_3c | T_3c_3h | T_3c_2c | T_PSM1h | T_PSM1c | T_PSM2h | T_PSM2c | T_PSM3h | T_PSM3c
A-1 | -6467.2614 | 13550.3449 | -6467.2614 | -615.8221 | 55.9168 | 45.653 | 56.1942 | 45.4418 | 55.9168 | 45.653 | 54.2389 | 45 | 65 | 45.6424 | 54.2389 | 45 | 9.0015 | -18.003 | 9.0015 | 10 | -10 | 10 | -93.0123 | -141.6358 | -93.0123 | 10 | -10 | 10 | -9.0015 | 9.0015 | 9.0015 | -18.003 | 9.0015 | 9.0015 | -9.0015 | 24.3117 | -24.3117 | -93.0123 | -141.6358 | -93.0123 | -24.3117 | 24.3117 | 55.9168 | 55.9168 | 56.1942 | 56.1942 | 56.1942 | 55.9168 | 55.9168 | 45.653 | 45.653 | 45.4418 | 45.4418 | 45.4418 | 45.653 | 45.653 | 54.2389 | 45 | 65 | 45.6424 | 54.2389 | 45
A-2 | -6249.0238 | 13153.0306 | -6249.0238 | -654.9831 | 61.4443 | 45.0059 | 61.9631 | 44.6631 | 61.4443 | 45.0059 | 53.9272 | 45 | 65 | 46.21 | 53.9272 | 45 | 5.4307 | -10.8613 | 5.4307 | 10 | -10 | 10 | -60.0696 | -77.7674 | -60.0696 | 10 | -10 | 10 | -5.4307 | 5.4307 | 5.4307 | -10.8613 | 5.4307 | 5.4307 | -5.4307 | 8.8489 | -8.8489 | -60.0696 | -77.7674 | -60.0696 | -8.8489 | 8.8489 | 61.4443 | 61.4443 | 61.9631 | 61.9631 | 61.9631 | 61.4443 | 61.4443 | 45.0059 | 45.0059 | 44.6631 | 44.6631 | 44.6631 | 45.0059 | 45.0059 | 53.9272 | 45 | 65 | 46.21 | 53.9272 | 45
A-3 | -7010.3818 | 13346.4739 | -5685.9671 | -650.125 | 60.8728 | 45.0419 | 61.3126 | 44.6997 | 60.7729 | 45.0025 | 55.0148 | 45 | 65 | 45.9336 | 53.1228 | 45 | 6.3261 | -11.4768 | 5.1507 | 10 | -10 | 10 | -45.9397 | -69.9554 | -54.0353 | 10 | -10 | 10 | -6.3261 | 5.1507 | 6.3261 | -11.4768 | 5.1507 | 6.3261 | -5.1507 | 12.0078 | -7.96 | -45.9397 | -69.9554 | -54.0353 | -12.0078 | 7.96 | 60.8728 | 60.8728 | 61.3126 | 61.3126 | 61.3126 | 60.7729 | 60.7729 | 45.0419 | 45.0419 | 44.6997 | 44.7472 | 44.6413 | 45.0025 | 45.0025 | 55.0148 | 45 | 65 | 45.9336 | 53.1228 | 45
A-4 | -6542.1826 | 13705.1719 | -6542.1826 | -620.8066 | 56.8317 | 45.3585 | 57.1447 | 45.1272 | 56.8317 | 45.3585 | 54.346 | 45 | 65 | 45.4212 | 54.346 | 45 | 8.146 | -16.292 | 8.146 | 10 | -10 | 10 | -135.1565 | -174.9767 | -135.1565 | 10 | -10 | 10 | -8.146 | 8.146 | 8.146 | -16.292 | 8.146 | 8.146 | -8.146 | 19.9101 | -19.9101 | -135.1565 | -174.9767 | -135.1565 | -19.9101 | 19.9101 | 56.8317 | 56.8317 | 57.1447 | 57.1447 | 57.1447 | 56.8317 | 56.8317 | 45.3585 | 45.3585 | 45.1272 | 45.1272 | 45.1272 | 45.3585 | 45.3585 | 54.346 | 45 | 65 | 45.4212 | 54.346 | 45
A-5 | -5685.9671 | 13346.4738 | -7010.3818 | -650.125 | 60.7729 | 45.0025 | 61.3126 | 44.6997 | 60.8728 | 45.0419 | 53.1228 | 45 | 65 | 45.9336 | 55.0148 | 45 | 5.1507 | -11.4768 | 6.3261 | 10 | -10 | 10 | -54.0353 | -69.9554 | -45.9397 | 10 | -10 | 10 | -5.1507 | 6.3261 | 5.1507 | -11.4768 | 6.3261 | 5.1507 | -6.3261 | 7.96 | -12.0078 | -54.0353 | -69.9554 | -45.9397 | -7.96 | 12.0078 | 60.7729 | 60.7729 | 61.3126 | 61.3126 | 61.3126 | 60.8728 | 60.8728 | 45.0025 | 45.0025 | 44.6997 | 44.6413 | 44.7472 | 45.0419 | 45.0419 | 53.1228 | 45 | 65 | 45.9336 | 55.0148 | 45
A-6 | -5998.6603 | 13563.3939 | -6946.1133 | -618.6204 | 56.3164 | 45.2246 | 56.6427 | 45.3874 | 56.3768 | 45.9197 | 53.5695 | 45 | 65 | 45.6237 | 54.923 | 45 | 7.726 | -17.2152 | 9.4892 | 10 | -10 | 10 | -121.5794 | -157.3996 | -103.3644 | 10 | -10 | 10 | -7.726 | 9.4892 | 7.726 | -17.2152 | 9.4892 | 7.726 | -9.4892 | 17.9101 | -27.0176 | -121.5794 | -157.3996 | -103.3644 | -17.9101 | 27.0176 | 56.3164 | 56.3164 | 56.6427 | 56.6427 | 56.6427 | 56.3768 | 56.3768 | 45.2246 | 45.2246 | 45.3874 | 44.9817 | 45.7176 | 45.9197 | 45.9197 | 53.5695 | 45 | 65 | 45.6237 | 54.923 | 45
A-7 | -6419.3344 | 13484.6039 | -6419.3344 | -645.9351 | 60.3028 | 45.0212 | 60.7612 | 44.7107 | 60.3028 | 45.0212 | 54.1705 | 45 | 65 | 45.7363 | 54.1705 | 45 | 6.001 | -12.002 | 6.001 | 10 | -10 | 10 | -41.3388 | -62.9492 | -41.3388 | 10 | -10 | 10 | -6.001 | 6.001 | 6.001 | -12.002 | 6.001 | 6.001 | -6.001 | 10.8052 | -10.8052 | -41.3388 | -62.9492 | -41.3388 | -10.8052 | 10.8052 | 60.3028 | 60.3028 | 60.7612 | 60.7612 | 60.7612 | 60.3028 | 60.3028 | 45.0212 | 45.0212 | 44.7107 | 44.7107 | 44.7107 | 45.0212 | 45.0212 | 54.1705 | 45 | 65 | 45.7363 | 54.1705 | 45
A-8 | -6946.1133 | 13563.3939 | -5998.6603 | -618.6204 | 56.3768 | 45.9197 | 56.6427 | 45.3874 | 56.3164 | 45.2246 | 54.923 | 45 | 65 | 45.6237 | 53.5695 | 45 | 9.4892 | -17.2152 | 7.726 | 10 | -10 | 10 | -103.3644 | -157.3996 | -121.5794 | 10 | -10 | 10 | -9.4892 | 7.726 | 9.4892 | -17.2152 | 7.726 | 9.4892 | -7.726 | 27.0176 | -17.9101 | -103.3644 | -157.3996 | -121.5794 | -27.0176 | 17.9101 | 56.3768 | 56.3768 | 56.6427 | 56.6427 | 56.6427 | 56.3164 | 56.3164 | 45.9197 | 45.9197 | 45.3874 | 45.7176 | 44.9817 | 45.2246 | 45.2246 | 54.923 | 45 | 65 | 45.6237 | 53.5695 | 45
A-9 | -9429.3303 | 13550.3449 | -3505.1925 | -615.8221 | 55.9168 | 40.9521 | 56.1942 | 45.4418 | 55.9168 | 50.3539 | 53.4705 | 40 | 65 | 45.6424 | 55.0074 | 50 | 9.0015 | -18.003 | 9.0015 | 10 | -10 | 10 | -93.0123 | -141.6358 | -93.0123 | 10 | -10 | 10 | -9.0015 | 9.0015 | 9.0015 | -18.003 | 9.0015 | 9.0015 | -9.0015 | 24.3117 | -24.3117 | -93.0123 | -141.6358 | -93.0123 | -24.3117 | 24.3117 | 55.9168 | 55.9168 | 56.1942 | 56.1942 | 56.1942 | 55.9168 | 55.9168 | 40.9521 | 40.9521 | 45.4418 | 40.7703 | 50.1132 | 50.3539 | 50.3539 | 53.4705 | 40 | 65 | 45.6424 | 55.0074 | 50
A-10 | -10547.825 | 21220.2667 | -10009.5689 | -662.8729 | 61.8962 | 45.1564 | 62.2114 | 45.3727 | 61.8962 | 46.0107 | 55.0455 | 45 | 65 | 49.8427 | 59.2994 | 45 | 9.0015 | -18.003 | 9.0015 | 15 | -20 | 10 | -93.0123 | -141.6358 | -93.0123 | 15 | -20 | 10 | -9.0015 | 9.0015 | 9.0015 | -18.003 | 9.0015 | 9.0015 | -9.0015 | 24.3117 | -24.3117 | -93.0123 | -141.6358 | -93.0123 | -24.3117 | 24.3117 | 61.8962 | 61.8962 | 62.2114 | 62.2114 | 62.2114 | 61.8962 | 61.8962 | 45.1564 | 45.1564 | 45.3727 | 44.9483 | 45.7972 | 46.0107 | 46.0107 | 55.0455 | 45 | 65 | 49.8427 | 59.2994 | 45